## MTEP Projects Under Evaluation
MTEP19 and MTEP20 Project List 2019-09-20
Target Appendix | App ABC | Planning Region | Geographic Location by TO Member System | PrjId | Project Name | Project Description | State1 | State2 | System Need | Preliminary Allocation Type per FF | Share Status | Preliminary Other Type | Expected ISD (Min) | Expected ISD (Max) | Max kV | Min kV | MISO Facility | Estimated Cost | Transmission Type
A in MTEP20 | B>A | South | AECC | 16884 | Helena Industrial Breaker Removal | Remove inline breaker at the AECC Helena Industrial Switching Station | AR | AR | System is being reconfigured, breaker will no longer be needed with new configuration | Other |  | Other Local Needs | 2021-06-01 | 2021-06-01 | 115 | 0 | Y | 150000 | Bottom-Up
A in MTEP20 | B>A | South | AECC | 17924 | Huffman 161/12.47 Substation | An existing industrial customer is expanding their production facilities to include 25 MW of new load. AECC will be tapping AECC 161 kV transmission line, constructing approximately 3 miles of 161 kV transmission line with 605 ACSS, and constructing the new Huffman 161/12.47 kV distribution substation to serve this load. | AR | AR | An existing industrial customer is expanding their production facilities to include 25 MW of new load. AECC will be tapping AECC 161 kV transmission line, constructing approximately 3 miles of 161 kV transmission line with 605 ACSS, and constructing the new Huffman 161/12.47 kV distribution substation to serve this load. | Other |  | Load Growth | 2021-09-01 | 2021-09-01 | 161 | 12.47 | Y | 4000000 | Bottom-Up
A in MTEP20 | B>A | South | Entergy-AR | 18094 | Hot Springs 115kV SPOF | Install dual primary protection on the 115 kV bus schemes at Hot Springs. | AR | AR | There is the potential for ~350 MW of load at risk around Hot Springs and ~150 MW of generator instability (Remmel, Blakely, Carpenter) to occur for a SLG fault on the Hot Springs 115 kV bus with non-redundant relay failure (NERC TPL-001-4 category P5 event). | BRP |  |  | 2022-06-01 | 2022-06-01 | 115 | 0 | Y | 2226434 | Bottom-Up
A in MTEP20 | B>A | South | Entergy-AR | 18097 | Pleasant Hill 500kV: Add 2 Reactors | Add 2 100 MVAR reactors at Pleasant Hill 500 kV bus | AR | AR | There is the potential for both ANO U1 and U2 to go unstable for a SLG stuck breaker fault (breaker B5106) at ANO 500 kV (NERC TPL-001-4 category P4 event), resulting in the loss of the ANO – Ft. Smith 500 kV and the ANO – Mabelvale 500 kV lines. When either unit absorbs reactive power, the unit(s) operates in a less stable state as compared to when the unit(s) operates at unity power factor or produces reactive power. The addition of the Pleasant Hill reactors will lessen the reactive power needed to be absorbed by the ANO units and thus improve the stability of the units. Without the Pleasant Hill reactors, the ANO units would each need to produce 25 MVARs to remain in a stable operating state (regardless of system voltages) when generating full MW output to withstand this P4 event. | BRP |  |  | 2023-06-01 | 2023-06-01 | 500 | 0 | Y | 15879463 | Bottom-Up
A in MTEP20 | B>A | South | Entergy-AR | 18099 | El Dorado 115kV: Underrated Breaker | Replace the 115 kV breaker(s) at El Dorado with 63 kA fault interrupting capability. B5820, B6258, B6758, B7158, and B7658 will be replaced. | AR | AR | MTEP20 short circuit analysis indicated five underrated breakers at the existing El Dorado EHV 115 kV substation. The breaker analysis was performed using the latest Entergy Planning short circuit model. | BRP |  |  | 2022-06-01 | 2022-06-01 | 115 | 0 | Y | 1508741 | Bottom-Up
A in MTEP20 | B>A | South | Entergy-AR | 18100 | Danville 161kV: Install Cap Bank | Install a 24 MVAR cap bank at Danville 161kV | AR | AR | Low voltage in the City of Dardanelle and Danville areas for the loss of SPA Dardanelle Dam – City of Dardanelle 161 kV & North Magazine – Blue Mountain 161 kV line sections. | Other |  | Reliability | 2023-06-01 | 2023-06-01 | 161 | 0 | Y | 1694575 | Bottom-Up
A in MTEP20 | B>A | South | Entergy-AR | 18101 | Hot Springs Plemmons 115kV: Construct new substation | Build a new 115kV substation with a single 40 MVA 115/13.8 kV LTC transformer. | AR | AR | The Hot Springs West 115kV Substation contains a single conventional 20.1/26.8/33.6 MVA, 115/13.8kV transformer with a 3330 kVA Voltage Regulator. The transformer serves four feeder breakers which feed into the urban area of Hot Springs, AR. In the summer of 2024, the transformer and regulator are projected to be loaded to 33.45 MVA (100% loaded) which exceeds the nameplate rating of the substation regulator. | Other |  | Load Growth | 2024-06-01 | 2024-06-01 | 115 | 13.8 | Y | 9776082 | Bottom-Up
A in MTEP20 | B>A | South | Entergy-AR | 18103 | Screeton 115kV: Construct new substation | Build a new 115kV substation with a single 40 MVA 115/13.8kV LTC transformer between Hazen and Carlisle 115kV substations near the town of Screeton. | AR | AR | The Hazen Substation has a single 20 MVA transformer with a 2000 kVA regulator serving three circuits. The substation had a 2018 peak load of 18.71 MVA (94% of capacity) and served 1700 customers. Additionally, the Hazen substation has a first contingency shortfall of 15 MVA affecting 1600 customers, with the shortfall growing to 17 MVA by 2022.The Carlisle substation has a first contingency shortfall of 14.3 MVA affecting 1500 customers, with the shortfall growing to 15 MVA in 2022. | Other |  | Load Growth | 2024-06-01 | 2024-06-01 | 115 | 13.8 | Y | 13809157 | Bottom-Up
A in MTEP19 | B>A | South | AECC | 10207 | Heber Springs North to Partain 161kV: New line | Build 5 position ring bus at the existing AECC Heber Springs North, build 26 mile 161kV line from the existing Heber Springs North substation to the proposed Partain 161/69kV substation. | AR | AR | Loop the proposed Partian substation and tie into a breaker station. Provide a means to serve Heber Springs North load for a P2 event at Heber Springs North and a means to serve Clinton West load for a P2 event at Clinton West (TPL-base line reliability). Also allows a looped feed into the proposed Partain 161/69kV substation. | Other |  | Reliability | 2023-02-01 | 2023-02-02 | 161 | 0 | Y | 38900000 | Bottom-Up
A in MTEP19 | B>A | South | AECC | 15668 | Tap EAI Hot Springs EHV - Woodward: Construct Sheridan West 115/13.2 kV substation | Construct 12 MVA, 115/13.2 kV substation under Entergy Hot Springs EHV - Woodward 115 kV transmission west of Sheridan, AR. | AR | AR | Distribution reliability need. New substation to be placed in load center to accommodate load growth in the Sheridan area. Also, existing load from Sheridan South will be transferred to new substation. | Other |  | Load Growth | 2022-01-01 | 2022-01-01 | 115 | 0 | Y | 2000000 | Bottom-Up
A in MTEP19 | B>A | South | AECC | 16904 | McDougal 161/24.9kV Substation | 161/24.9kV 16MVA distribution substation on Entergy's Corning to Texas Eastern 161kV line. | AR | AR | Increased Capacity | Other |  | Load Growth | 2020-12-01 | 2020-12-01 | 161 | 0 | Y | 3000000 | Bottom-Up
A in MTEP19 | B>A | South | AECC | 17084 | Pocahontas Industrial Park Tap | Pocahontas Industrial Park Substation is currently being served out of Pocahontas East. Entergy requested this Pocahontas Industrial Park line to be re-routed into Baltz Lake Switching Station to reduce line exposure and increase system reliability. For operational flexibility, a Pocahontas Industrial Park Tap switch is being added to maintain the capability of the current topology (serving this line out of Pocahontas East). Also as a result of this project, this creates an alternate path for the 161kV network system between Baltz Lake Switching Station and Pocahontas East which allows flexibility during maintenance or outage scenarios. | AR | AR | Operational Flexibility | Other |  | Reliability | 2019-12-31 | 2019-12-31 | 161 | 0 | Y | 50000 | Bottom-Up
A in MTEP19 | B>A | South | AECC | 17085 | Partian to Heber Springs North 69kV line rebuild | Rebuild existing 69kV line from the proposed Partain 161/69kV substation to the existing Heber Springs North 161/69kV substation. | AR | AR | The 40+ year old 69kV line is in disrepair (failing poles, cross-arms, and conductor). This a cost saving project because it is being rebuilt in parallel with the Partain to Heber Springs North 161kV line using the same ROW and structures. | Other |  | Age and Condition | 2023-02-01 | 2023-02-01 | 69 | 0 | Y | 15000000 | Bottom-Up
A in MTEP19 | B>A | South | AECC | 17610 | Moro thru path maintenance | Perform maintenance on thru path changing bus conductor, switches, and MODs. | AR | AR | Old station in need of maintenance | Other |  | Reliability | 2020-06-01 | 2020-06-01 | 69 | 0 | Y | 300000 | Bottom-Up
A in MTEP19 | B>A | South | Entergy-AR | 12050 | Amity Tap 115kV: Add Transmission Breakers | Build a 115kV breaker station at the Amity 115kV tap location | AR | AR | Enhanced project to reduce customer interruptions due to a 78 mile long breaker to breaker transmission line with 12,500 customers. A 28 mile radial tap with 3 substations on this breaker to breaker line. | Other |  | Reliability | 2023-06-01 | 2023-06-01 | 115 | 0 | Y | 9611792 | Bottom-Up
A in MTEP19 | B>A | South | Entergy-AR | 12053 | Batesville 161kV: Add Transmission Breakers | Build a new station adjacent to Batesville 161kV substation which is located between ISES 161kV and Sage 161kV substations. | AR | AR | There is 45 miles of transmission exposure breaker to breaker which includes a 10 mile tap line to Cave City. There are 14,000 customers on this transmission line. This is to reduce customer interruptions on the long line. | Other |  | Reliability | 2024-06-01 | 2024-06-01 | 161 | 0 | Y | 9000000 | Bottom-Up
A in MTEP19 | B>A | South | Entergy-AR | 13612 | Little Rock Enhanced Reliability Project Phase 2 | Rebuild ~3.8 miles of the LR 8th and Woodrow - LR Palm Street - LR West 115kV lines to a minimum of 1950 Amps. | AR | AR | LR Gaines - LR west 115kV line overloads over 180% when the LR South - LR Rock Creek and LR Kanis - LR West Markham 115kV lines are out of service. This condition would require up to 150 MW's of load shed to relieve the thermal overload on the lines. There are multiple other N-2's in this area that cause 50 - 150 Mw's of load at risk that will also be addressed with this project. | Other |  | Reliability | 2025-06-01 | 2025-06-01 | 115 | 0 | Y | 14021893 | Bottom-Up
A in MTEP19 | B>A | South | Entergy-AR | 13613 | Little Rock Enhanced Reliability Project Phase 1 | Rebuild ~2.2 miles of the LR Gaines - LR 8th and Woodrow 115kV line to a minimum of 1950 Amps. | AR | AR | LR Gaines - LR west 115kV line overloads over 180% when the LR South - LR Rock Creek and LR Kanis - LR West Markham 115kV lines are out of service. This condition would require up to 150 MW's of load shed to relieve the thermal overload on the lines. There are multiple other N-2's in this area that cause 50 - 150 Mw's of load at risk that will also be addressed with this project. | Other |  | Reliability | 2024-06-01 | 2024-06-01 | 115 | 0 | Y | 8375693 | Bottom-Up
A in MTEP19 | B>A | South | Entergy-AR | 15564 | Hot Springs Village - Sierra 115kV Rebuild | Upgrade ~1 mile of Hot Springs - Sierra 115kV line and terminal equipment to obtain a minimum flow through rating of 1300 Amps (259 MVA). | AR | AR | Hot Springs Village - Sierra 115kV line, rated at 106 MVA, overloads for the loss of the ANO - Fort Smith 500 kV and AEPW Flint Creek generation. [NERC TPL - 001-4 P3.2] Hot Springs Village - Sierra 115kV line also overloads for the loss of ANO - Fort Smith 500 kV in the Summer 2026 model. [NERC TPL - 001-4 P1.2] | BRP |  |  | 2020-12-30 | 2020-12-30 | 115 | 0 | Y | 2131351 | Bottom-Up
A in MTEP19 | B>A | South | Entergy-AR | 15565 | Laney Road 115kV New Substation | Build a new 115/13.8kV substation with a 40 MVA 115/13.8kV transformer. Install a new 2000 amp main breaker and new 13.8kV low side operating and transfer buses. | AR | AR | Provide improved reliability for the town of Junction City and the surrounding area. Reduce voltage dips for the Union County Lumber and Great Lakes Chemical facilities. Reduce the load at risk at the El Dorado Upland substation for the loss of T2. Eliminate first contingency load at risk on the El Dorado Upland feeder A210. Reduce the load at risk on the El Dorado Newell A216 circuit. | Other |  | Reliability | 2024-06-01 | 2024-06-01 | 115 | 13.8 | Y | 11200000 | Bottom-Up
A in MTEP19 | B>A | South | Entergy-AR | 16244 | Bellaire 115kV: Construct Switching Station (J620) | Construct a three breaker 115kV ring bus on the Macon Lake - Dermott 115kV line section to facilitate the J620 Solar facility interconnection. There will be remote relay setting changes performed as well. | AR | AR | A new three breaker 115kV ring bus is needed to interconnect the J620 Solar Facility. | GIP |  |  | 2020-03-18 | 2020-03-18 | 115 | 0 | Y | 8258000 | Externally Driven
A in MTEP19 | B>A | South | Entergy-AR | 16246 | Crossett South 115kV: Construct Switching Station (J680) | The existing Crossett South 115kV switching station, on the Crossett North - Sterlington 115kV line, will be converted to a four breaker ring bus switching station to accommodate the interconnection of J680 Solar Facility. The line trap at Crossett North 15kV will be removed. Relay settings will be updated at the Sterlington 115kV substation. | AR | AR | A 4 breaker 115kV ring bus switching station is needed to interconnect J680 Solar Facility. | GIP |  |  | 2021-04-15 | 2021-04-15 | 115 | 0 | Y | 9976000 | Externally Driven
A in MTEP19 | B>A | South | Entergy-AR | 16247 | Crooked Lake 161kV: Install Transmission Breaker and Line Bay (J586) | Expand the existing Crooked Lake 161kV Substation with a new line bay and breaker. | AR | AR | The substation expansion is needed to accommodate the J586 Solar Facility. | GIP |  |  | 2021-03-01 | 2021-03-01 | 161 | 0 | Y | 3845000 | Externally Driven
A in MTEP19 | B>A | South | Entergy-AR | 16248 | Lee 115kV: Construct Switching Station (J552) | Construct a new three breaker 115kV ring bus station on the Brinkley East - Moro 115kV line. New relay settings will be required at the remote end station of Brinkley East and West Helena. | AR | AR | The new switching station is needed to accommodate the J552 solar facility. | GIP |  |  | 2021-06-01 | 2021-06-01 | 115 | 0 | Y | 7858000 | Externally Driven
A in MTEP19 | B>A | South | Entergy-AR | 16249 | Ashley 115kV: Construct Switching Station (J603) | A new three breaker 115kV ring bus will be constructed on the AECC Mist - Montrose 115kV line. New relays panels and settings will be needed at Crossett North. New line traps will be installed at Hamburg and Montrose. Also a relay panel will be replaced at the Lake Village Bagby station. | AR | AR | This new 115kV 3 breaker ring bus is needed to accommodate the J603 Solar Facility. | GIP |  |  | 2021-09-15 | 2021-09-15 | 115 | 0 | Y | 8887000 | Externally Driven
A in MTEP20 | B>A | West | ITCM | 9100 | Burlington-4th St-Agency 69kV Rebuild | Rebuild a portion of the Burlington-South Burlington 69kV line and upgrade the Burlington 69kV terminal so the Burlington-South Burlington line is conductor limited. Rebuild the Burlington 4th Street-Agency 69kV line to T2-477 ACSR. | IA | IA | Single contingency that will overload the Burlington-South Burlington 69kV and the 4th Street-Agency 69kV lines without restricting generation output in the area. |  |  |  | 2021-05-31 | 2021-05-31 | 69 | 69 | Y |  | Bottom-Up
A in MTEP20 | B>A | West | ITCM | 16710 | J233 J514 GIA Amendment Network Upgrades | The J233 GIA has been amended to include J514, a 65 MVW increase in ERIS and 30 MW of NRIS for the Marshalltown Generating Station. Network upgrades include raising spans on the Marshalltown-Blairstown 115kV and the Blairstown-Prairie Creek 115kV. | IA | IA | Amended GIA has been signed. | GIP |  |  | 2019-12-31 | 2019-12-31 | 115 | 115 | Y | 2732821 | Externally Driven
A in MTEP20 | B>A | West | ITCM | 16844 | J495 Generator Interconnection | ITCM and EDF have entered into an engineering and procurement agreement for the acquisition of materials and design of a 3-terminal, 3 breaker, 345 kV switching station to be constructed roughly 7 miles east of the Ledyard 345 kV station and connected to the Ledyard to Colby 345 kV line. The E&P agreement will cover the design and material acquisition for the 345 kV station, and construction work will occur under the GIA. | IA | IA | GIA signed | GIP |  |  | 2019-10-18 | 2019-10-18 | 345 | 345 | Y | 10662026 | Externally Driven
A in MTEP20 | B>A | West | ITCM | 16864 | J475 Generator Interconnection | The Poweshiek to Irvine 161 kV line is to be rebuilt on existing ROW with a conductor having a minimum summer rating of 1,595A. Upgrades at the Poweshiek 161 kV substation will also be required. | IA | IA | GIA signed. | GIP |  |  | 2020-10-01 | 2020-10-01 | 161 | 161 | Y | 11000000 | Externally Driven
A in MTEP20 | B>A | West | ITCM | 16865 | J504 Generator Inteconnection | The DAEC 161 kV substation will be expanded to accommodate the J504 terminal, including the addition of breaker position 5953. New equipment should be capable of 2000A. | IA | IA | The GIA between ITCM, Duane Arnold Solar, LLC (NextEra Energy) and MISO has been executed to facilitate the interconnection of project J504, a 60 MVA solar generating facility rated 51 MW gross and 50MW net with a Point of Interconnection at the DAEC 161 kV substation. | GIP |  |  | 2020-10-15 | 2020-10-15 | 161 | 161 | Y | 273780 | Externally Driven
A in MTEP20 | B>A | West | ITCM | 16866 | J498/J499/J500 Generator Interconnection | One span on the Poweshiek - Reasnor kV line will be raised to mitigate sag limits and increase the summer rating to 366 MVA (1313 A). | IA | IA | GIA signed | GIP |  |  | 2019-12-01 | 2019-12-01 | 161 | 161 | Y | 240000 | Externally Driven
A in MTEP20 | B>A | West | ITCM | 17704 | Cedar Rapids Hunter Field Substation Interconnection | IPL will be building a new 69/24.9 kV substation named Cedar Rapids Hunter Field near the existing Viola’s Corner substation. This new substation will replace Viola’s Corner. The new substation will have 1 new 69/24.9 kV 50 MVA transformer installed initially, with a second transformer to be added in the future as load grows in the area. ITC will build a new 69 kV substation with two single box structures and two breakers installed, one line breaker and one bus tie breaker, and will add an additional line breaker in the future when IPL adds a second transformer. | IA | IA | Customer requested interconnection |  |  |  | 2021-12-30 | 2021-12-30 | 69 | 25 | Y |  | Bottom-Up
A in MTEP20 | B>A | West | ITCM | 17705 | Madrid North 69kV Substation Rebuild Interconnection | IPL has requested ITC to rebuild the Madrid North Substation to a standard single box and double box with a bus tie breaker to accommodate their 25 kV plans which will include two transformers and 25 kV switchgear. ITC will also need to install a new control enclosure, as IPL will be retiring their existing control enclosure to accommodate their new switch gear. The existing 69 kV circuit switcher will be replaced with a new 69 kV breaker, which will allow for future retirement of the bus work associated with the 69/34.5 kV transformer. The existing zig-zag transformer should be removed to allow additional space for the installation of the new ITC owned control enclosure. The 69/34.5 kV transformer will need to remain until the conversion to 69 kV happens between Dawson and Madrid North (covered on EI Sketch ITCMW_16_034). The existing section of 69 kV bus that feeds the 69/34.5 kV transformer, transformer, and low-side breaker should be re-used, and then removed in the future as part of the 69 kV conversion. | IA | IA | Customer requested interconnection |  |  |  | 2021-12-31 | 2021-12-31 | 69 | 34 | Y |  | Bottom-Up
A in MTEP20 | B>A | West | ITCM | 17724 | Sixth Street 115kV Substation Retirement | Once the remaining 34.5 kV lines at the Sixth St Substation are converted to 69 kV, the remaining substation equipment should be retired, including any control enclosures and fence, etc. The 34.5 kV lines will be connected to bypass the substation as part of the conversion work, but the 115 kV lines will need to be connected to bypass the substation as part of the substation retirement project. The communications currently routed through Sixth Street will also need to be moved/removed before the retirement can be completed. | IA | IA | 34.5kV to 69kV conversion will remove all the 34kV lines out of the Sixth Street substation. In order to retire the Sixth Street substation the 115kV lines will need to be rerouted to bypass the site. |  |  |  | 2023-01-31 | 2023-12-31 | 115 | 34 | Y | 1506540 | Bottom-Up
A in MTEP20 | B>A | West | ITCM | 17732 | Eddyville Industrial Complex 161kV Substation Expansion | ITC will expand the Eddyville Industrial Complex 161kV substation to the north. As part of the straight bus expansion, ITCM will install three new 161kV breakers. In addition, ITC will terminate the Beacon – Tri County and EIC – Tri County 161kV circuits into these breakers. | IL | IA | In order to improve system reliability and mitigate an N-1-1 issue at the Cargill Eddyville plant. |  |  |  | 2025-12-31 | 2025-12-31 | 161 | 161 | Y |  | Bottom-Up
A in MTEP20 | B>A | West | ITCM | 17733 | J504 Generator Inteconnection-TOIF | The GIA between ITCM, Duane Arnold Solar, LLC (NextEra Energy) and MISO has been executed to facilitate the interconnection of project J504, a 60 MVA solar generating facility rated 51 MW gross and 50MW net with a Point of Interconnection at the DAEC 161 kV substation. The Interconnection Customer is responsible for costs associated with the TOIF. | IA | IA | GIA executed | GIP |  |  | 2020-10-15 | 2020-10-15 | 161 | 161 | Y | 0 | Externally Driven
A in MTEP20 | B>A | West | ITCM | 17734 | Clinton Perrin 69/24kV Substation Interconnection | IPL requested a new Clinton Perrin 69/24kV substation in Clinton, IA. The new substation in city of Clinton, will provide capacity for industrial load south/west of town and will support retirement of Beaver Channel sub and Mill Creek sub after 25kV conversion. IPL will install a single transformer, 12.5kV substation, 20/33MVA capacity. Transformer will have 25kV option, but will be replaced by a 30/50MVA unit for final 25kV configuration. Installed XFMR will be moved elsewhere at that time. This conversion is estimated to be 10-20 years after completion of this construction. Four feeders will be used from this substation to serve load. Contingency at 12.5kV will be up to max rating of transformer, 33MVA. Contingency at 25kV will be reviewed and updated at a later date, but may be up to future 50MVA top rating of final unit. | IA | IA | Customer requested interconnection |  |  |  | 2023-12-31 | 2023-12-31 | 69 | 24 | Y |  | Bottom-Up
A in MTEP20 | B>A | West | ITCM | 17735 | Clinton South 69kV Substation Retirement | Retire all ITC owned equipment in the Clinton South 69/distribution sub and reroute the 69kV line to bypass the Clinton South sub. | IA | IA | Customer requested interconnection. Once the Clinton Perrin sub is online, the load from the Clinton South sub will be move to the new Perrin source and the Clinton South sub will then be retired. |  |  |  | 2024-12-31 | 2024-12-31 | 69 | 69 | Y |  | Bottom-Up
A in MTEP20 | B>A | West | ITCM | 17736 | Waukon Snakeskin 69kV Substation Interconnection | IPL will be constructing the Waukon Snakeskin 2 transformer 69/25kV substation the replace the nearby Waukon substation. ITC will install 2 box structures, 2 line breakers and 1 tie breaker. The cap bank and cap bank breaker at the existing Waukon substation should be moved to the Decorah side of the Waukon Snakeskin substation if possible or a new cap bank and breaker of equivalent effective rating should be installed. All substation equipment should have a minimum rating of 1200A. ITC will also install short in/out tap lines. | IA | IA | Customer requested interconnection |  |  |  | 2021-12-31 | 2021-12-31 | 69 | 69 | Y | 2507447 | Bottom-Up
A in MTEP20 | B>A | West | ITCM | 17738 | Thompson MacTavish 69kV Substation Interconnection | ITC will install an ~0.02 mile tap line to IPL’s new Thompson MacTavish 69/24.9kV Distribution Substation. This substation will be Open Air Single Bus with a 12/20MVA 69/24.9kV transformer and high side breaker. The substation will be located on one of the two land options available to IPL. The Thompson and Buffalo Center substations will be retired on future EI sketches once IPL moves the loads from those substations to Thompson MacTavish. Coordinate with IPL and DPC for outages. | IA | IA | Customer requested interconnection |  |  |  | 2025-12-31 | 2025-12-31 | 69 | 69 | Y | 346800 | Bottom-Up
A in MTEP20 | B>A | West | ITCM | 17739 | Calmar Prairie Farmer 69kV Substation Interconnection | ITC will install an ~0.02 mile tap line to IPL’s new Calmar Prairie Farmer 69/24.9kV Distribution Substation. The transformer will have a highside breaker installed by IPL. This substation will be located near the existing Calmar substation. IPL has provided four proposed locations. The Calmar and Ossian substations will be retired on future EI sketches once IPL moves the loads from those substations to Calmar Prairie Farmer. | IA | IA | Customer requested interconnection |  |  |  | 2021-12-31 | 2021-12-31 | 69 | 69 | Y |  | Bottom-Up
A in MTEP20 | B>A | West | ITCM | 17980 | Hancock T3 161/69kV Transformer Replacement | Replace the Beaver Channel T1 & T2 75MVA 161/69kV transformers with the spare 150MVA 161/69kV transformer (SN: WT03583) currently located at the Ames substation. Also install a high side breaker for the new transformer at Beaver channel and replace switch 1454. Any new high side equipment should be 1200A minimum and any new low side equipment should be 1600A minimum. Replace the Hancock T3 75MVA 161/69kV transformer with the Beaver Channel T1 75MVA 161/69kV Transformer (SN: 70450A). Also replace the high side circuit switcher 1320 with a 161kV circuit breaker. Re-use switch 1320B if feasible. Any other new required high-side equipment should be 1200A minimum. | IA | IA | The Hancock T3 transformer is failing and has gassing concerns needs to be replaced as soon as possible to avoid a forced outage under peak load. The 75MVA size is smaller that the ITC standard size and the larger units will not match the impedance of the other Hancock 75MVA unit that has not failed. Beaver Channel has two 75 MVA transformers in parallel and one is very old and is on the maintenance schedule to be replace within 3-5 years. Best use of the Beaver Channel transformers will be to move the newer 75MVA unit to Hancock and retire the older bad unit. Then replace the parallel units with a new 150 MVA standard size transformer. |  |  |  | 2020-04-30 | 2020-04-30 | 161 | 69 | Y | 4589958 | Bottom-Up
A in MTEP20 | B>A | West | ITCM | 18061 | Mason City Industrial 161kV Substation Interconnection | ITCM will interconnect Alliant Energy’s Mason City Industrial 161/24.9kV distribution substation with in/out taps to the Emery-Lime Creek 161kV line and install four (4) 161kV breakers in a ring bus configuration at the 161kV distribution substation. IPL will install a single distribution transformer initially to serve a load of ~18MW. IPL will install a second distribution transformer in the future to accommodate load growth and load moved from 69kV distribution substations. | IA | IA | Customer requested interconnection |  |  |  | 2022-05-30 | 2022-05-30 | 161 | 24.9 | Y |  | Bottom-Up
A in MTEP20 | B>A | West | MEC | 18050 | Sub 77: Add 161 kV Circuit Breaker | Add new 161 kV circuit breaker at Sub 77 on the 161 kV line terminal to Sub 91. | IA | IA | The Sub 77 161-13.2 kV distribution transformer is presently located on the Sub 77-Sub 91 161 kV line terminal such that faults on the 161 kV line also outage the transformer. Adding a 161 kV circuit breaker to separate the 161 kV line from the transformer improves the reliability of service to distribution customers served from Sub 77. |  |  |  | 2021-12-01 | 2021-12-01 | 161 | 0 | Y | 800000 | Bottom-Up
A in MTEP20 | B>A | West | MEC | 18117 | Washburn-Hazleton 161 kV Reconductor | Reconductor Washburn-Hazleton 161 kV line. Upgrade Washburn substation terminal equipment. | IA | IA | MISO DPP 2016 FEB West identified network upgrade |  |  |  | 2020-10-31 | 2020-10-31 | 161 | 0 | Y | 16700000 | Bottom-Up
A in MTEP20 | B>A | West | MEC | 18119 | Lundquist-Deere Northeast 161 kV Uprate | Replace terminal equipment at Deere Northeast substation to increase 161 kV line rating. | IA | IA | MISO DPP 2016 FEB West identified network upgrade |  |  |  | 2020-10-31 | 2020-10-31 | 161 | 0 | Y | 50000 | Bottom-Up
A in MTEP20 | B>A | West | MEC | 18121 | Deere Northeast-Washburn 161 kV Uprate | Replace limiting substation terminal equipment at Deere Northeast and Washburn to increase the rating of the Deere Northeast-Washburn 161 kV line. | IA | IA | MISO DPP 2016 FEB West identified network upgrade |  |  |  | 2020-10-31 | 2020-10-31 | 161 | 0 | Y | 100000 | Bottom-Up
A in MTEP20 | B>A | West | MEC | 18124 | Sub T FD-Boone Jct 161 kV Reconductor | Reconductor MidAmerican's portion of the Sub T FD-Boone Jct 161 kV line and upgrade substation terminal equipment at Sub T FD. | IA | IA | MISO DPP 2016 FEB West identified network upgrade |  |  |  | 2020-12-31 | 2020-12-31 | 161 | 0 | Y | 7322500 | Bottom-Up
A in MTEP20 | B>A | West | MEC | 18125 | Grimes-Beaver Creek 345 kV Uprate | Replace structures to uprate the Grimes-Beaver Creek 345 kV line. | IA | IA | MISO DPP 2016 FEB West identified network upgrade |  |  |  | 2020-12-31 | 2020-12-31 | 345 | 0 | Y | 753000 | Bottom-Up
A in MTEP20 | B>A | West | MEC | 18126 | Franklin-Wall Lake 161 kV Uprate | Replace structures to uprate the Franklin-Wall Lake 161 kV line. | IA | IA | MISO DPP 2016 FEB West identified network upgrade |  |  |  | 2020-06-30 | 2020-06-30 | 161 | 0 | Y | 220000 | Bottom-Up
A in MTEP20 | B>A | West | MEC | 18127 | Sycamore: 345 kV Equipment Upgrades | At the Sycamore substation, replace two 345 kV circuit breakers, associated disconnect switches, and jumpers to increase the rating of the Grimes-Sycamore 345 kV south line. | IA | IA | MISO DPP 2016 FEB West identified network upgrade |  |  |  | 2021-06-30 | 2021-06-30 | 345 | 0 | Y | 1200000 | Bottom-Up
A in MTEP20 | B>A | West | MEC | 18128 | Raun: Retire 345 kV Reactor | Retire the 345 kV reactor at the Raun Substation. | IA | IA | The switching device on the 345 kV reactor at Raun no longer operates properly. |  |  |  | 2021-12-01 | 2021-12-01 | 345 | 0 | Y | 110000 | Bottom-Up
A in MTEP20 | B>A | West | MEC | 18129 | 25th Street NW 161 KV Substation | Construct a new 161 kV substation and associated 161 kV line work to source customer-owned transformation and new load. | IA | IA | Substation is needed to serve customer-owned substation and large load. |  |  |  | 2022-07-01 | 2022-07-01 | 161 | 0 | Y | 12935000 | Bottom-Up
A in MTEP20 | B>A | West | MEC | 18137 | South Waukee 161-13.2 kV Substation | Construct a new 161-13.2 kV distribution substation and associated 161 kV line work to accommodate area growth. | IA | IA | Distribution substation is needed to serve increasing levels of area load. |  |  |  | 2022-06-01 | 2022-06-01 | 161 | 13.2 | Y | 11988000 | Bottom-Up
A in MTEP20 | B>A | West | MEC | 18151 | Granger Tap-100th St & 54th Ave 161 kV Reconductor | Reconductor Granger Tap-100th St & 54th Ave 161 kV line with T2-795 ACSR Drake. | IA | IA | MISO DPP 2016 FEB West identified network upgrade |  |  |  | 2021-06-30 | 2021-06-30 | 161 | 0 | Y | 2085000 | Bottom-Up
A in MTEP20 | B>A | West | MEC | 18174 | Bondurant-Montezuma 345 kV Uprate | Replace structures to uprate the Bondurant-Montezuma 345 kV line. | IA | IA | MISO DPP 2016 FEB West identified network upgrade |  |  |  | 2020-06-30 | 2020-06-30 | 345 | 0 | Y | 320000 | Bottom-Up
A in MTEP20 | B>A | West | MEC | 18176 | Ciruit Breaker Additions and Replacements 2020-2022 | Blanket project to add and replace new 345 kV circuit breakers to expand to ring bus which will reduce misoperations, increase reliability and operating flexibility. | IA | IA | Three-year "blanket project" to add new 345 kV circuit breakers and replace existing 345 kV circuit breakers at several existing substations to increase system reliability and operating flexibility. This also involves conversion of straight bus to a ring bus. The circuit breaker additions will reduce misoperations, replaces aging infrastructure, and reduces maintenance costs. Specific project locations and scope of work to be determined on an ongoing basis as determined by need. |  |  |  | 2022-12-01 | 2022-12-01 | 345 | 0 | Y | 31000000 | Bottom-Up
A in MTEP20 | B>A | West | MEC | 18177 | Webster-Sub T FD 161 kV Reconductor | Reconductor portion of Webster-Sub T Fort Dodge 161 kV line. | IA | IA | MISO DPP 2016 FEB West identified network upgrade |  |  |  | 2021-12-15 | 2021-12-15 | 161 | 0 | Y | 6300000 | Bottom-Up
A in MTEP20 | B>A | West | MEC | 18181 | Black Hawk 345 kV Capacitor | Add 345 kV, 150 MVAR capacitor bank at Black Hawk 345 kV. | IA | IA | MISO DPP 2016 FEB West identified network upgrade |  |  |  | 2021-12-31 | 2021-12-31 | 345 | 0 | Y | 4500000 | Bottom-Up
A in MTEP20 | B>A | West | MEC | 18183 | Midport 161 kV Capacitor | Add 161 kV, 50 MVAR capacitor at Midport. Includes addition of 161 kV circuit breakers on 161 kV line terminals. | IA | IA | MISO DPP 2016 FEB West identified network upgrade |  |  |  | 2021-06-30 | 2021-06-30 | 161 | 0 | Y | 1545000 | Bottom-Up
A in MTEP20 | B>A | West | MEC | 18185 | Montezuma 345 kV Capacitor | Add 345 kV, 100 MVAR capacitor bank at Montezuma 345 kV. | IA | IA | MISO DPP 2016 FEB West identified network upgrade |  |  |  | 2021-12-31 | 2021-12-31 | 345 | 0 | Y | 4150000 | Bottom-Up
A in MTEP20 | B>A | West | MEC | 18186 | Deep River 161 kV Capacitor | Add 161 kV, 25 MVAR capacitor at Deep River (J438 POI) 161 kV substation. | IA | IA | MISO DPP 2016 FEB West identified network upgrade |  |  |  | 2021-06-30 | 2021-06-30 | 161 | 0 | Y | 1175000 | Bottom-Up
A in MTEP20 | B>A | West | MEC | 18188 | Diamond Trail-Hills 345 kV Uprate | Replace structures to uprate the Diamond Trail (J530 POI) - Hills 345 kV line. | IA | IA | MISO DPP 2016 FEB West identified network upgrade |  |  |  | 2020-06-30 | 2020-06-30 | 345 | 0 | Y | 350000 | Bottom-Up
A in MTEP20 | B>A | West | MEC | 18280 | Floyd 161-69 kV Transformer Terminal Upgrade | Replace terminal equipment adjacent to Floyd Substation 161-69 kV Transformer AB. | IA | IA | Increase thermal rating. |  |  |  | 2020-11-01 | 2020-11-01 | 161 | 69 | Y |  | Bottom-Up
A in MTEP20 | B>A | South | SMPA | 18232 | Rice - 69kV breakers and relaying | Replace (3) aging breaker and relaying | IA | IA | Needed due to age of the breakers |  |  |  | 2020-12-31 | 2020-12-31 | 69 | 0 | Y | 850000 | Bottom-Up
A in MTEP19 | B>A | West | ITCM | 10785 | Beaver Channel-Rock Creek 161kV Reconductor | ITC will reconductor the Beaver Channel-Rock Creek 161kV 3.68 mile line to 366 MVA capacity and upgrade the Beaver Channel 161kV terminal 140 and the Rock Creek 161kV terminal 171. This will also require modifying the 69kV circuit that is on the same structures. | IA | IA | The 2018 retirement of the ML Kapp generation formerly served out of the Beaver Channel substation has impacted system flows in the Clinton, IA area. Several N-1-1 or P6 contingencies in the Clinton, IA area cause the Beaver Channel-Rock Creek 161kV line to overload. | BRP |  |  | 2022-12-31 | 2022-12-31 | 161 | 69 | Y | 3299102 | Bottom-Up
A in MTEP19 | B>A | West | ITCM | 15004 | New London Tap 69kV Rebuild | Rebuild the existing 69kV New London tap to current 69kV standards using T2(2-4/0) conductor along existing route. | IA | IA | The New London tap was constructed with long spans and no shield wire approximately 47 years ago. This has resulted in poor reliability of not only the tap but also the main line between Burlington North and Mediapolis as there is no breaker on the tap. This condition cannot be corrected with maintenance. | Other |  | Age and Condition | 2022-12-31 | 2022-12-31 | 69 | 69 | Y | 6140000 | Bottom-Up
A in MTEP19 | B>A | West | ITCM | 15024 | Huntwoods-Sawyer IAAP 69kV Rebuild | Re-route the line segment requiring maintenance by constructing approximately 4.4 new miles of T2(2-4/0) 69kV line beginning at Huntwoods and heading west and then south tying into the existing Huntwoods-Sawyer. Retire approximately 3.5 miles of existing 69kV line beginning at Huntwoods and heading southwest to the point where the new line will tie into the existing line. | IA | IA | A 3.5 mile segment of the Huntwoods-Sawyer 69kV line located on Iowa Army Ammunition Plant (IAAP) property is in poor condition and requires maintenance. A significant portion of this line segment cannot be accessed to replace poles and other equipment requiring replacement. | Other |  | Other Local Needs | 2020-12-31 | 2020-12-31 | 69 | 69 | Y | 6463262 | Bottom-Up
A in MTEP19 | B>A | West | ITCM | 15446 | Toledo Central 69kV Substation Interconnection | Two (2) 69kV breakers will be installed at the Toledo Central Substation. All the substation equipment will be rated for 1200A or greater. IPL will purchase the land for the Toledo Central Substation. IPL will install one 69-34.5/25kV 33MVA transformer at the substation. | IA | IA | Customer requested load interconnection needed to facilitate the conversion to 69kV operation. | Other |  | Load Growth | 2023-12-30 | 2023-12-30 | 69 | 25 | Y | 1375320 | Bottom-Up
A in MTEP19 | B>A | West | ITCM | 15447 | Belle Plaine North 69kV Substation Interconnection | ITC Midwest will build the 69kV portion of the new Belle Plaine North 69kV substation. The new substation will be a three breaker in-and-out design with two 69-34/25kV distribution transformers. The new substation will also require OPGW to be installed on the Belle Plaine Jct-Belle Plaine North line and the Belle Plaine North-River Valley line. | IA | IA | The 34.5kV system is aged and in poor condition in many locations, as well as unable to adequately serve new loads that may want to connect in the area due to limited available capacity. ITCM is working to upgrade the 34.5kV system to 69kV operation, which will greatly increase available capacity and decrease system losses. This project is to interconnect the new Belle Plaine North Substation as requested by Alliant Energy and is part of the overall plan to convert the area to 69kV operation. | Other |  | Age and Condition | 2023-12-31 | 2023-12-31 | 69 | 69 | Y | 3889715 | Bottom-Up
A in MTEP19 | B>A | West | ITCM | 15448 | Williamsburg West 161kV Substation Interconnection | The Williamsburg West Substation will be a 161kV Five (5) Position Ring Bus. All 161kV equipment will be capable of 2000A or greater. IPL will purchase the property. IPL will be installing two (2) 25kV 20 MVA distribution transformers at Williamsburg West. The Williamsburg Transmission Substation will be fed from Williamsburg West until the conversion to 69kV. The Williamsburg Transmission Substation will be retired as part of the conversion to 69kV. Williamsburg West will be a PD Substation. | IA | IA | Long term plan to convert 34.5kV system to 69kV operation. | Other |  | Age and Condition | 2022-12-30 | 2022-12-30 | 161 | 161 | Y | 4425776 | Bottom-Up
A in MTEP19 | B>A | West | ITCM | 15449 | Ottumwa Heights 161kV Substation Interconnection | As part of a long term plan to shift the load in Ottumwa off the 69kV and onto the 161kV system, IPL and ITC will be building a 161:26.2/13.1kV substation near Rutledge substation. IPL will purchase the land and own the joint use assets. ITCMW will construct a 4-position ring bus. All terminal equipment should be capable of 2000A minimum. ITC will build two independent taps from Ottumwa Generation – Woody #1 to the Ottumwa Heights substation. | IA | IA | At the request of Alliant Energy, ITCM will interconnect a new 161kV distribution substation on the northeast side of Ottumwa, IA. The city of Ottumwa is expecting continued load growth and transmission is required to support this load growth. This new substation is the beginning of a multi-year plan to shift the load off the existing 69kV. | Other |  | Load Growth | 2021-12-31 | 2021-12-31 | 161 | 161 | Y | 9774134 | Bottom-Up
A in MTEP19 | B>A | West | ITCM | 15450 | Beaver Rock 69kV Terminal Addition | Construct a new line terminal at the Beaver Rock substation. CIPCO will construct a new 69kV line (~13.5 miles) from the Buffalo Bill REC substation to the Beaver Rock substation (potentially using existing lines/ structures). This will create a second networked line between Beaver Rock and Grand Mound. MEC may also need to retire a portion(s) of the line between Sub 55, Sub 73, and Beaver Rock. | IA | IA | Customer requested load interconnection. | Other |  | Load Growth | 2021-12-31 | 2021-12-31 | 69 | 69 | Y | 279755 | Bottom-Up
A in MTEP19 | B>A | West | ITCM | 15451 | Mt Vernon 161-69kV Transformer Addition | At Mount Vernon substation a 100 MVA 161/69 kV transformer will be installed. Also two 161 kV line breakers will be installed. The 161/34.5 kV transformer will remain until after all of the 34.5 kV loads are converted to 69 kV. | IA | IA | The 34.5 kV system is aged and in poor condition in many locations, as well as unable to adequately serve new loads that may want to connect in the area due to limited available capacity. ITCM is working to upgrade the 34.5 kV system to 69 kV operation, which will greatly increase available capacity and decrease system losses. | Other |  | Age and Condition | 2022-06-01 | 2022-06-01 | 161 | 69 | Y | 6747636 | Bottom-Up
A in MTEP19 | B>A | West | ITCM | 15452 | Anamosa White Fawn Substation 69kV Interconnection | IPL will be constructing a 69x34.5 / 13.2 kV substation just north of the city of Anamosa, IA. IPL’s substation will be designed as a two (2) transformer substation but only one (1) will be installed in the near term. ITCM will install one (1) 69 kV breaker and associated equipment and tap and re-route the Amber Creamery Ckt. 6270 to create an in and out transmission configuration with a conductor having a minimum rating of 640 Amps. | IA | IA | Customer requested load interconnection associated with the 34.5kV to 69kV conversion work. | Other |  | Load Growth | 2019-12-31 | 2019-12-31 | 69 | 34 | Y | 1477036 | Bottom-Up
A in MTEP19 | B>A | West | ITCM | 15453 | Clarence South 69kV Substation Interconnection | ITCM will install one (1) 69 kV breaker and associated equipment at IPL’s Clarence South substation location and two ~0.02 mile tap lines. All 69 kV equipment needs to have a minimum rating of 1200A. Note: The 69 kV breaker needs to be installed on the Olin side of the Clarence South XFMR. Work with IPL to determine the location of the box structure. | IA | IA | Customer requested load interconnection associated with the 34.5kV to 69kV conversion. | Other |  | Load Growth | 2022-12-31 | 2022-12-31 | 69 | 69 | Y | 2137117 | Bottom-Up
A in MTEP19 | B>A | West | ITCM | 15454 | Walford Terry 69kV Substation Interconnection | The Walford Terry Substation will be a new substation with three (3) 69kV terminals capable of 1200A or greater. One (1) future capacitor position will be needed. Staging and size of the capacitor bank will be finalized in a future EI Sketch. IPL will be installing a 69-34.5/25kV 12.5MVA transformer at the substation. IPL requested a position is reserved for a position for a mobile transformer. IPL will be purchasing the substation location. | IA | IA | Customer requested load interconnection associated with the 3.45kV to 69kV conversion. | Other |  | Load Growth | 2022-12-30 | 2022-12-30 | 69 | 69 | Y | 2720948 | Bottom-Up
A in MTEP19 | B>A | West | ITCM | 15455 | Dysart-Traer 161kV Rebuild | ITC Midwest will rebuild the existing 15.93 mile 161kV circuit with T2 Hawk conductor, which will significantly decrease the susceptibility to violent galloping. ITC Midwest is also rebuilding the 34.5kV circuit from Dysart to Traer to 69kV which will generally follow the same route. In an effort to address the age and condition concerns for both the 34.5kV and 161kV circuits, portions of these lines will be built to double circuit. | IA | IA | The existing Dysart – Traer 161kV circuit has had several operations and maintenance issues in the past. These issues have stemmed from the use of Pheonix SD conductor and the age/class of the poles. In the past couple years ITC has attached several different anti-galloping devices which hasn’t eliminated the issues. ITC Midwest is also rebuilding the 34.5kV circuit from Dysart to Traer to 69kV which will generally follow the same route. In an effort to address the age and condition concerns for both the 34.5kV and 161kV circuits, portions of these lines will be built to double circuit. | Other |  | Age and Condition | 2021-12-31 | 2021-12-31 | 161 | 69 | Y | 26474400 | Bottom-Up
A in MTEP19 | B>A | West | ITCM | 15456 | Brooklyn-Malcom 69kV line & Grinnell 69kV Terminal | ITC Midwest will construct a new ~9 mile 69kV line from Brooklyn to the Malcom Tap, install new 69kV switches at the Malcom substation, and rebuild 1 mile of line from the Malcom Tap to the Grinnell Substation to double circuit 69kV. ITC Midwest will add a 69kV terminal and breaker at the Grinnell substation. | IA | IA | The 34.5 kV system is aged and in poor condition in many locations, as well as unable to adequately serve new loads that may want to connect in the area due to limited available capacity. ITCM is working to upgrade the 34.5 kV system to 69 kV operation, which will greatly increase available capacity and decrease system losses. | Other |  | Age and Condition | 2026-12-30 | 2026-12-31 | 69 | 69 | Y | 10686722 | Bottom-Up
A in MTEP19 | B>A | West | ITCM | 15484 | Solon Big Grove 69kV Interconnection | ITC will install two new ~0.08 mile tap lines from the CIPCO owned 34.5kV line to the IPL owned Solon Big Grove (new) distribution substation. The tap line will be initially operated at 34.5kV but should be constructed to 69kV standards due to the future conversion from Eagle to Mt. Vernon. CIPCO will install 69kV switches on the main line. ITC will install a highside 69kV bus and one (1) 69kV breaker. The breaker will be located on the Eagle side of the transformer. All necessary outages should be coordinated with IPL and CIPCO. | IA | IA | Customer requested load interconnection. | Other |  | Load Growth | 2020-12-31 | 2020-12-31 | 69 | 34 | Y | 2358250 | Bottom-Up
A in MTEP19 | B>A | West | ITCM | 15485 | Asbury 161kV Breaker Additions | Add two 161kV line breakers, and a 161kV bus tie breaker, and a new control enclosure at the Asbury substation. Install OPGW from the Lore substation to the Asbury substation on the 2.95 mile Lore-Asbury 161kV line section. | IA | IA | The N-1 (P1) loss of the Lore-Asbury-Center Grove 161kV line will outage both 161/13kV Asbury distribution transformers. Alliant Energy has requested ITC install 161kV breakers at the Asbury substation to increase the reliability of the Asbury distribution transformers. Currently one Asbury distribution transformer is used to back up the other Asbury distribution transformer. The loss of both units is difficult to back up on the distribution system and can not be done under peak load conditions. In addition, planned maintenance is difficult to perform at the Asbury substation. | Other |  | Reliability | 2021-12-31 | 2021-12-31 | 161 | 161 | Y | 4267200 | Bottom-Up
A in MTEP19 | B>A | West | ITCM | 15486 | South Grandview 161kV Breaker Additions | Add two 161kV line breakers, a bus tie breaker, and a new control enclosure at the South Grandview substation. | IA | IA | Customer requested. Alliant Energy has requested that ITC install 161kV breakers at the South Grandview substation. A single initiating event N-1 (P1) loss of the Salem-South Grandview-8th Street 161kV line will outage both 161/13kV South Grandview distribution transformers. Currently one South Grandview distribution transformer is used to back up the other South Grandview distribution transformer. The loss of both units is difficult to back up on the distribution system and can not be done under peak load conditions. | Other |  | Reliability | 2020-12-31 | 2020-12-31 | 161 | 161 | Y | 2928000 | Bottom-Up
A in MTEP19 | B>A | West | ITCM | 16685 | Nevada 19th Street Expansion | Alliant Energy requests ITC to replace the existing 69 kV single breaker, motor operated switch and 69 kV structures with two standard single box structures with two line breakers and a tie breaker which will allow space for Alliant Energy to install transformer primary circuit breakers and will improve reliability. To facilitate these changes, ITC will likely need a separate control building as space is limited in the existing control building. | IA | IA | IPL will install a 2nd transformer and distribution bus in the existing substation to serve a new 5 MW load addition in the area. Total area load at this substation is 15 MW. In addition, this substation must provide critical backup to Nevada North substation which also provides backup to Lincoln Hwy Industrial Substation. The schedule requires the new equipment to be on line by April 1, 2020. Customer requested load interconnection. | Other |  | Load Growth | 2020-04-01 | 2020-04-01 | 69 | 69 | Y | 2259124 | Bottom-Up
A in MTEP19 | B>A | West | ITCM | 16686 | Garner Galls Creek 161kV Interconnection | ITC will construct a 4 position ring bus with a 36 MVAR rated (27.6 MVAR effective) capacitor bank that shares a position with one of IPL’s transformers. | IA | IA | IPL has requested to connect a new substation “Garner Galls Creek” on the Emery-Hancock 161kV line. Customer requested load interconnection. | Other |  | Load Growth | 2020-09-30 | 2020-09-30 | 161 | 161 | Y | 5330370 | Bottom-Up
A in MTEP19 | B>A | West | ITCM | 16687 | Clinton 2nd Ave-Clinton North 6 mile 69kV Rebuild | Rebuild ~6.1 miles of old 4/0 ACSR line from the Clinton 2nd Ave sub to the Clinton North sub and retire the Clinton 2nd Street-Clinton South 69kV line. | IA | IA | Customer requested line removal. (see project justification document) | Other |  | Other Local Needs | 2021-06-01 | 2021-06-01 | 69 | 69 | Y | 5411800 | Bottom-Up
A in MTEP19 | B>A | West | MEC | 14784 | 50th Avenue NW Substation | New 161 kV distribution substation, associated 161 kV line reconfiguration and construction, and conversion of Bondurant Substation 161 kV bus to breaker-and-a-half configuration. | IA | IA | Distribution substation is needed to serve increasing levels of customer load. | Other |  | Load Growth | 2020-08-01 | 2020-08-01 | 161 | 13 | Y | 21031000 | Bottom-Up
A in MTEP19 | B>A | West | MEC | 15664 | Indian Creek East 161 kV Substation Expansion | Expand the 161 kV ring bus and install two 161 kV circuit breakers and one transformer terminal. | IA | IA | Provides a utility connection point to a newly installed customer-owned transformer. | Other |  | Load Growth | 2019-11-01 | 2019-11-01 | 161 | 0 | Y | 2000000 | Bottom-Up
A in MTEP19 | B>A | West | MEC | 15665 | Overland Trail-Bunge 161 kV Line | Construct a new 161 kV line between the Overland Trail and Bunge Substations and add new 161 kV line terminals at Bunge and Overland Trail | IA | IA | Mitigates potential overloading of the CBEC-Overland Trail 161 kV line after P6 contingency at high wind generation. Provides a second strong source to the River Bend and Bunge Substations. | MPFP |  |  | 2020-06-01 | 2020-06-01 | 161 | 0 | Y | 9300000 | Externally Driven
A in MTEP19 | B>A | West | MEC | 15667 | Southland 345 kV Substation Expansion | Add two new 345 kV circuit breakers and two transformer terminals. | IA | IA | Provides a utility connection point for customer-owned transformers. | Other |  | Load Growth | 2019-12-01 | 2019-12-01 | 345 | 0 | Y | 3800000 | Bottom-Up
A in MTEP19 | B>A | West | MEC | 15669 | Sub 701: Install 2nd 161-69 kV Transformer | Install a second 161-69 kV transformer and complete the 161 kV ring bus at Sub 701. Install two new 161 kV circuit breakers. | IA | IA | Reduces post-contingent loading on the existing Sub 701 161-69 kV transformer. | Other |  | Reliability | 2021-06-01 | 2021-06-01 | 161 | 0 | Y | 4200000 | Bottom-Up
A in MTEP19 | B>A | West | MEC | 15670 | Glenwood: Rebuild 69 kV Substation | Rebuild the Glenwood 69-13.2 kV Substation to improve reliability. | IA | IA | Previous equipment failures have affected service reliability at this older substation. | Other |  | Age and Condition | 2020-12-01 | 2020-12-01 | 69 | 13 | NT | 400000 | Bottom-Up
A in MTEP19 | B>A | West | MEC | 15672 | Maffitt Lake 161-13 kV Substation | Construct a new 161-13 kV substation and 9.5 miles of associated 161 kV line taps. | IA | IA | New large customer load. | Other |  | Load Growth | 2020-06-01 | 2020-06-01 | 161 | 13 | Y | 23700000 | Bottom-Up
A in MTEP19 | B>A | West | MEC | 15673 | SE Magazine Road 161-13 kV Substation | Construct a new SE Magazine Road 161-13 kV distribution substation tapping the Ankeny to NE Ankeny 161 kV line. | IA | IA | Serves new customer load. | Other |  | Load Growth | 2020-06-01 | 2020-06-01 | 161 | 13.2 | Y | 1100000 | Bottom-Up
A in MTEP19 | B>A | West | MEC | 15674 | John Deere West 69-13 kV Substation | Construct a new John Deere West 69-13 kV distribution substation adjacent to the existing John Deere Substation and retire the existing John Deere Substation. | IA | IA | Serve existing customer load. This reliability improvement project replaces the existing John Deere Substation. | Other |  | Reliability | 2020-06-01 | 2020-06-01 | 69 | 13.2 | NT | 4900000 | Bottom-Up
A in MTEP19 | B>A | West | MEC | 15675 | Dakota City 69 kV Switching Station | New Dakota City four-terminal 69 kV Switching Station tapping the MidAmerican Energy Humboldt East-Thor 69 kV line and the Corn Belt Power Cooperative Galbraith to Hope 69 kV line. | IA | IA | Mitigates low voltages and thermal overloads after maintenance outage and Category P1 contingencies during off-peak load conditions. | Other |  | Reliability | 2020-06-01 | 2020-06-01 | 69 | 0 | NT | 4900000 | Bottom-Up
A in MTEP19 | B>A | West | MEC | 15676 | Webster-Hayes 161 kV Structure Replacements | Replace structures on the Webster to Hayes 161 kV line to increase conductor clearances. | IA | IA | The line rating increase resulting from this project is to address post-contingent overloads following local P6 N-1-1 contingencies. | GIP |  |  | 2020-06-01 | 2020-06-01 | 161 | 0 | Y | 175000 | Externally Driven
A in MTEP19 | B>A | West | MEC | 15677 | Foster Road 161-13 kV Substation | Construct a new Foster Road 161-13 kV distribution substation bisecting the Sub P-Northgate 161 kV line. | IA | IA | Serve growing customer load. | Other |  | Load Growth | 2020-06-01 | 2020-06-01 | 161 | 13 | Y | 1850000 | Bottom-Up
A in MTEP19 | B>A | West | MEC | 15679 | Sub 56: New 161 kV Line Terminal | Add a new 161 kV line terminal at Sub 56 for a new CIPCO/MPW 161 kV line to Muscatine, Iowa. | IA | IA | The line terminal is needed to connect a new 161 kV line being built by Central Iowa Power Cooperative (CIPCO) and Muscatine Power & Water (MPW). | Other |  | Reliability | 2021-06-01 | 2021-06-01 | 161 | 0 | Y | 900000 | Bottom-Up
A in MTEP19 | B>A | West | MEC | 15680 | Sub A-Sub 84-Sub 55 69 kV Line Uprate | Replace structures to increase the allowable operating temperature of the line conductor on the Sub A-Sub 84 and Sub 84-Sub 55 69 kV lines | IA | IA | Addresses post-contingent loading following local Category P6 (N-1-1) contingencies. | Other |  | Reliability | 2019-09-01 | 2019-11-01 | 69 | 0 | NT | 600000 | Bottom-Up
A in MTEP19 | B>A | West | MEC | 15681 | Raun Substation: Retire Reactor and Install Reactor Switchers | Retire one 13 kV reactor connected to the tertiary of Raun 345-161 kV transformer AC and install new reactor switchers on the two remaining 13 kV reactors. | IA | IA | Needed to mitigate failed equipment and reduce switching transient overvoltages. | Other |  | Other Local Needs | 2019-12-31 | 2019-12-31 | 13 | 0 | Y | 550000 | Bottom-Up
A in MTEP19 | B>A | West | MEC | 15682 | Neal South 161 kV Tap Lines | Bisect the Neal North-Salix Junction 161 kV line and construct a new double circuit 161 kV line into Neal South, Expand the Neal South substation and install two new 161 kV line terminals. | IA | IA | Mitigates potential low voltages after a P6 contingency. | BRP |  |  | 2020-06-01 | 2020-06-01 | 161 | 0 | Y | 6500000 | Bottom-Up
A in MTEP19 | B>A | West | MEC | 15683 | Merrill North Substation Transformer and Line | Expand the Merrill North Substation 69 kV bus to install a second 69-12.47 kV transformer and second 69 kV line. Install two 69 kV line breakers and construct second 69 kV line into Merrill North Substation. Retire the existing Merrill Substation. | IA | IA | Failure of equipment at Merrill 69 kV Substation. | Other |  | Age and Condition | 2020-12-01 | 2020-12-01 | 69 | 0 | NT | 900000 | Bottom-Up
A in MTEP19 | B>A | West | MEC | 15684 | Kellogg-Plymouth 69 kV Line Uprate | Replace structures on the Plymouth-Kellogg 69 kV line to increase the line rating. | IA | IA | The Kellogg-Plymouth 69 kV line can overload for a P1 contingency. | Other |  | Reliability | 2020-12-31 | 2020-12-31 | 69 | 0 | NT | 250000 | Bottom-Up
A in MTEP19 | B>A | West | MEC | 15690 | Buena Vista: Replace CT on Wisdom 161 kV Line Terminal | Replace a CT (current transformer) on the Wisdom 161 kV line terminal at Buena Vista Substation. | IA | IA | This CT appears as a limiter in PROMOD studies. | Other |  | Other Local Needs | 2020-12-31 | 2020-12-31 | 161 | 0 | Y | 17000 | Bottom-Up
A in MTEP19 | B>A | West | MEC | 15822 | New Sharon-Poweshiek 69 kV Reconductor and Replace Structures | Reconductor and replace structures, as appropriate, on the New Sharon-Poweshiek 69 kV line. | IA | IA | MISO DPP 2015 August West Network Upgrade. | GIP |  |  | 2018-12-31 | 2018-12-31 | 69 | 0 | Y | 2400000 | Externally Driven
A in MTEP19 | B>A | West | MEC | 15824 | M Avenue-New Sharon 69 kV Reconductor and Replace Structures | Reconductor and replace structures, as appropriate, on the M Avenue to New Sharon 69 kV line. | IA | IA | MISO DPP 2015 August West Network Upgrade. | GIP |  |  | 2019-04-01 | 2019-04-01 | 69 | 0 | Y | 2100000 | Externally Driven
A in MTEP19 | B>A | West | MEC | 16545 | Ponderosa 161-13 kV Substation | Construct a new Ponderosa 161-13 kV Substation. | IA | IA | The substation is needed to serve increasing distribution load near Lake Ponderosa in east-central Iowa. | Other |  | Load Growth | 2021-06-01 | 2021-06-01 | 161 | 13 | Y | 2800000 | Bottom-Up
A in MTEP19 | B>A | West | MEC | 16605 | Gilbertville 161-13 kV Substation | Construct a new 10/13.3. MVA Gilbertville 161-13 kV distribution substation on the Washburn-Hazleton 161 kV line approximately 3.1 miles east of Washburn Substation | IA | IA | The existing 69-13 kV Gilbertville Substation is loaded to near its maximum 2.5 MVA capacity and is subject to flooding. The new Gilbertville 161-13 kV substation will provide increased load serving capability and will not be located in a flood plain. | Other |  | Load Growth | 2020-06-01 | 2020-06-01 | 161 | 13.2 | Y | 1305000 | Bottom-Up
A in MTEP19 | B>A | West | MPW | 15495 | MPW West - CIPCO Muscatine Switch - MEC Sub 56 161 kV Line | New 161 kV line from MPW West Sub to Muscatine Switching Sub CIPCO – Chappel Sub CIPCO – Bluegrass Sub CIPCO – Sub 56 MEC is to be built. In addition to the line MPW will be adding a new 161/69 kV auto transformer at Muscatine Switching Sub rated for 134.4 MVA. Existing 69 kV line from Fair Substation CIPCO to Chappel Sub CIPCO to Bluegrass Sub CIPCO will be retired and converted to 161 kV. Chappel Sub and Bluegrass Sub will be converted to 161 kV. This will then be the new 161 kV line path which will go into MEC Sub 56. The new 161 kV line will be passing by Fair substation but not connecting. | IA | IA | Prevent low voltages when MPW generation is off with a new 161 kV source into MPW local system. | Other |  | Other Local Needs | 2021-09-15 | 2021-09-15 | 161 | 69 | Y | 8300000 | Bottom-Up
B in MTEP20 | B | West | MEC | 16546 | Obrien County-Lakefield Jct. 345 kV Uprate | Raise selected structures on the Obrien County-Lakefield Junction 345 kV line. This will increase conductor ground clearances to obtain higher conductor operating ratings. | IA | IA | This project is needed to reduce potential future transmission flowgate congestion, based on economic planning studies conducted in MidAmerican Energy's local area planning process. | Other |  | Other Local Needs | 2019-12-31 | 2019-12-31 | 345 | 0 | Y | 400000 | Bottom-Up
B in MTEP19 | B | West | ITCM | 15826 | Lansing 161-69kV Transformer Upgrade | Move the Glenworth 161/69kV transformer to the Lansing substation and upgrade the terminal equipment to a minimum of 143MVA capacity. | IA | IA | The N-1-1 (P6) contingencies that outage multiple 161kV lines out of the Lansing substation will overload the existing Lansing 161/69kV 75MVA transformer. The only mitigation currently is to turn down the Lansing generation if any one of the 161kV lines at Lansing is out of service for any reason. | Other |  | Reliability | 2020-12-31 | 2020-12-31 | 161 | 69 | Y |  | Bottom-Up
B in MTEP19 | B | West | MEC | 15606 | Bondurant Breaker DAH806 Replacement | Replace 161 kV circuit breaker DAH806 at Bondurant Substation with a 40 kA circuit breaker. | IA | IA | The available fault current at this location is projected to exceed the interrupting duty of the existing circuit breaker at this location. | BRP |  |  | 2024-06-01 | 2024-06-01 | 161 | 0 | Y | 300000 | Bottom-Up
B in MTEP19 | B | West | MEC | 15607 | Sycamore Circuit Breaker DAG803 Replacement | Replace existing circuit breaker DAG803 at Sycamore Substation with a 63 kA unit. | IA | IA | The available fault current at this location is projected to exceed the interrupting capability of existing circuit breaker DAG803. | BRP |  |  | 2024-06-01 | 2024-06-01 | 161 | 0 | Y | 300000 | Bottom-Up
A in MTEP20 | B>A | West | ITCM | 17740 | ITCM Asset Blanket for 2023 | Replace equipment that is past its expected design life, utilizes outdated functionality or whose failure rates and maintenance have increased potential for misoperations and higher maintenance costs associated with their ongoing use. | IA,MN,IL | IA,MN,IL | Replace aging and outdated equipment on a cycle that will ensure each system is replaced near its expected end of life. Modern equipment can improve reliability, use state of the art technology, and typically will use longer maintenance intervals which reduces maintenance costs. Equipment is commonly equipped with better monitoring and alarming functionality giving improved remote supervision. |  |  |  | 2023-12-31 | 2023-12-31 | 345 | 69 | Y | 37080000 | Bottom-Up
A in MTEP20 | B>A | West | ITCM | 17741 | ITCM Customer Interconnects with short lead time 2023 | These projects are being done at the request of an interconnection customer in order to facilitate new load, re-distribute existing load, improve the performance of the sub-transmission and distribution systems, or to accommodate a new Transmission-to-Transmission connection request. | IA,MN,IL | IA,MN,IL | These projects are being done at the request of an interconnection customer in order to facilitate new load, re-distribute existing load, improve the performance of the sub-transmission and distribution systems, or to accommodate a new Transmission-to-Transmission connection request. |  |  |  | 2023-12-31 | 2023-12-31 | 345 | 69 | Y | 2400000 | Bottom-Up
A in MTEP19 | B>A | West | ITCM | 15444 | ITCM Asset Replacement Program 2022 | Replace equipment that is past its expected design life, utilizes outdated functionality or whose failure rates and maintenance have increased potential for misoperations and higher maintenance costs associated with their ongoing use. | IA,MN,IL | IA,MN,IL | Replace aging and outdated equipment on a cycle that will ensure each system is replaced near its expected end of life. Modern equipment can improve reliability, use state of the art technology, and typically will use longer maintenance intervals which reduces maintenance costs. Equipment is commonly equipped with better monitoring and alarming functionality giving improved remote supervision. | Other |  | Age and Condition | 2022-12-31 | 2022-12-31 | 345 | 69 | Y | 37080000 | Bottom-Up
A in MTEP19 | B>A | West | ITCM | 15445 | ITCM Customer Interconnects with short lead time 2022 | These projects are being done at the request of an interconnection customer in order to facilitate new load, re-distribute existing load, improve the performance of the sub-transmission and distribution systems, or to accommodate a new Transmission-to-Transmission connection request. | IA,MN,IL | IA,MN,IL | These projects are being done at the request of an interconnection customer in order to facilitate new load, re-distribute existing load, improve the performance of the sub-transmission and distribution systems, or to accommodate a new Transmission-to-Transmission connection request. | Other |  | Load Growth | 2022-12-31 | 2022-12-31 | 345 | 69 | Y | 2400000 | Bottom-Up
A in MTEP20 | B>A | Central | AmerenIL | 3012 | Normal East Substation Terminal Upgrade | Normal East 138/34 kV Substation - Upgrade 600 A terminal equipment to minimum 1200 A SE capability in the Brokaw-Normal East 138 kV line terminal. | IL | IL | P6-1-1: Overload to liniting terminal equipment for outage to South Bloomington-West Washington and Brokaw-South Bloomington 138 kV Line 1596. |  |  |  | 2020-06-01 | 2020-06-01 | 138 | 0 | Y | 900000 | Bottom-Up
A in MTEP20 | B>A | Central | AmerenIL | 9723 | Fishhook Breaker Station | Construct 138 kV breaker station in East Quincy-Meredosia-2 138 kV line. | IL | IL | Needed to facilitate connection by PPI |  |  |  | 2019-06-01 | 2019-06-01 | 138 | 138 | Y | 10900000 | Bottom-Up
A in MTEP20 | B>A | Central | AmerenIL | 9734 | North Utica Substation | Construct 138 kV breaker station in North LaSalle-Fox River-1646 138 kV line. | IL | IL | Needed to serve local load |  |  |  | 2023-12-01 | 2023-12-01 | 138 | 34.5 | Y |  | Bottom-Up
A in MTEP20 | B>A | Central | AmerenIL | 11925 | New Massac Substation - Convert Joppa 230 kV substation to 345 kV substation | Install 345/161 kV, 560 MVA transformer, remove 230/161 kV equipment. Rebuild Joppa-West Frankfort 230 kV for 345 kV use (Massac-Jordan). | IL | IL | Increased reliability |  |  |  | 2023-06-01 | 2023-06-01 | 345 | 161 | Y |  | Bottom-Up
A in MTEP20 | B>A | Central | AmerenIL | 11926 | New Jordan Substation - Convert West Frankfort 230 kV substation to 345 kV substation | Install 345/138 kV, 560 MVA transformer. Rebuild/reinsulate 19.9 miles of existing 230 kV line between West Frankfort and St. Johns for use at 345 kV. | IL | IL | Increased reliability |  |  |  | 2023-12-01 | 2023-12-01 | 345 | 138 | Y |  | Bottom-Up
A in MTEP20 | B>A | Central | AmerenIL | 11969 | New Miles-Misissippi 138 kV line | Construct new 138 kV line | IL | IL | Increased reliability |  |  |  | 2020-12-01 | 2020-12-01 | 138 | 0 | Y |  | Bottom-Up
A in MTEP20 | B>A | Central | AmerenIL | 12176 | Reconfigure West Frankfort East 345 kV to BAAH and add reactor | Reconfigure West Frankfort East to BAAH and install 345 kV, 50 Mvar shunt reactor. | IL | IL | Local area voltage control during light load conditions following transmission contingency event. Increased reliability and operating flexibility in the West Frankfort area. |  |  |  | 2023-06-01 | 2023-06-01 | 345 | 0 | Y | 14300000 | Bottom-Up
A in MTEP20 | B>A | Central | AmerenIL | 13689 | Upgrade Louisville South-Newton 138 kV line | Increase ground clearance for 20.49 miles of 954 ACSR rail in order to permit operation at 120 degrees C. Replace 954 ACSR rail bus conductor at both Louisville South and Newton. | IL | IL | Loading greater than 100% for an outage of Mt. Vernon-Xenia and Casey-Newton 345 kV lines. | BRP |  |  | 2023-12-01 | 2023-12-01 | 138 | 0 | Y |  | Bottom-Up
A in MTEP20 | B>A | Central | AmerenIL | 13705 | North Nashville Substation: Install 138 kV Ring Bus | Install initial 3 position 138 kV ring bus (ultimate 4 position) at North Nashville Substation. | IL | IL | Increase reliability and operating flexibility. Overloads and low voltages in the area under N-1-1 conditions. |  |  |  | 2021-12-01 | 2021-12-01 | 138 | 0 | Y | 7810000 | Bottom-Up
A in MTEP20 | B>A | Central | AmerenIL | 13708 | New Athens Dutch Hill 138 kV substation ring bus | Add 138 kV ring Bus. Initial 3-position (ultimate 4-position) | IL | IL | Increase reliability and operating flexibility in the area. |  |  |  | 2022-12-01 | 2022-12-01 | 138 | 0 | Y | 8376000 | Bottom-Up
A in MTEP20 | B>A | Central | AmerenIL | 13709 | New Putnam breaker-and-a-half 138 kV substation | Build new 138 kV BAAH substation on new site near Hennepin. | IL | IL | Age and condition of existing equipment and increase reliability in the area. |  |  |  | 2023-12-01 | 2023-12-01 | 138 | 0 | Y | 32492000 | Bottom-Up
A in MTEP20 | B>A | Central | AmerenIL | 13793 | New El Paso 138 kV substation ring bus | Install initial 4-postion ring bus at El Paso Substation for in/out supply. | IL | IL | Increase reliability and operating flexibility. |  |  |  | 2022-12-01 | 2022-12-01 | 138 | 0 | Y |  | Bottom-Up
A in MTEP20 | B>A | Central | AmerenIL | 13797 | Rebuild Albion South-Norris City North 138 kV to double circuit | Rebuild the existing 138 kV circuit to 2000A. Double circuit the line for new 3000A 345 kV circuit. | IL | IL | Age and condition reqquires replacement of structures. |  |  |  | 2022-12-01 | 2022-12-01 | 345 | 138 | Y | 74000000 | Bottom-Up
A in MTEP20 | B>A | Central | AmerenIL | 15265 | Reconfigure Carbondale NE 138 kV substation to ring bus | Install initial 3-position ring bus at Carbondale NE Substation | IL | IL | Increased reliability for the distribution system in the area and increased operating flexibility for the transmission system. |  |  |  | 2023-12-01 | 2023-12-01 | 138 | 0 | Y |  | Bottom-Up
A in MTEP20 | B>A | Central | AmerenIL | 15266 | Reconfigure Fayetteville Bee Hollow 138 kV substation to ring bus | Install initial 3-position ring bus at the existing Fayetteville Bee Hollow substation location. | IL | IL | Increased reliability on the area distribution system and increased operating flexibility on the transmission system. |  |  |  | 2023-12-01 | 2023-12-01 | 138 | 0 | Y |  | Bottom-Up
A in MTEP20 | B>A | Central | AmerenIL | 15504 | New Dempsey (Blue Mound) 138 kV ring bus addition | Install new ring bus at the tap to Blue Mound on the Pana-Route 51 Decatur-1462 line. | IL | IL | Station will provide reliability and system operating flexibility improvements as well as being the interconnection point for the J872 Decatur Wind project. |  |  |  | 2022-06-01 | 2022-06-01 | 138 | 0 | Y |  | Bottom-Up
A in MTEP20 | B>A | Central | AmerenIL | 16556 | New Bueller 138 kV substation (formerly Grove) | Tap the Macomb West-Niota 138 kV line to install a new ring bus station to supply the PPI Disco Substation. | IL | IL | Requested by PPI to connect their DISCO Substation. |  |  |  | 2023-12-02 | 2023-12-02 | 138 | 0 | Y | 8500000 | Bottom-Up
A in MTEP20 | B>A | Central | AmerenIL | 16704 | Salem West-Mt Vernon West-1332 138 kV line: Rebuild line to 2000A | Rebuild line to 2000A. Upgrade terminal equipment at Salem West to 2000A including 1272 ACSR bus conductor and switch 1330. | IL | IL | Increased reliability - This project will address congestion in the MISO RT and DA markets. |  |  |  | 2023-12-01 | 2023-12-01 | 138 | 0 | Y |  | Bottom-Up
A in MTEP20 | B>A | Central | AmerenIL | 16705 | Pana-Shelbyville South-1430 138 kV line: Rebuild line to 2000A | Rebuild line to 2000A capability. Upgrade terminal equipment at Shelbyville South to 2000A including re-tapping CTs and replacing 954 ACSR bus conductor. | IL | IL | Increased reliability - This project will address congestion in the MISO RT and DA markets. | [5 empty] | 138 | 0 | Y |  | Bottom-Up
A in MTEP20 | B>A | Central | AmerenIL | 16706 | Goose Creek: Rebuild the 345 kV ring bus to 3000A | Rebuild the Goose Creek 345 kV ring bus to 3000A capability. Replace all limiting terminal equipment and bus conductors with equipment capable of 3000A. | IL | IL | Increased reliability - This project will address congestion in the MISO RT and DA markets. |  |  |  | 2023-12-01 | 2023-12-01 | 345 | 0 | Y |  | Bottom-Up
A in MTEP20 | B>A | Central | AmerenIL | 16707 | New Kazad 138 kV Substation in St. Joseph area | Install new ring bus substation at the intersection of VERM-NCMP-1396 and GIFF-SDNY-1588. Install 4 positions initial, 6-positions ultimate. Rebuild the existing Vermillion-N. Champaign-1396 138 kV line to 2000A in both directions from the new substation. Upgrade terminal equipment at Vermillion to 2000A including switch 1328, bus conductor and relay load limit. Upgrade terminal equipment at North Champaign to 2000A including 795 AAC bus conductor and re-tap 1 CT. | IL | IL | Increased reliability - This project will address congestion in the MISO RT and DA markets. 134.79% loading on Vermillion-N. Champaign with N-1-1 outage of Hoopston-Rossville-1620 and Bunsonville-West Tilden in 2023 LL case for 2019 analysis. |  |  |  | 2023-12-01 | 2023-12-01 | 138 | 0 | Y |  | Bottom-Up
A in MTEP20 | B>A | Central | AmerenIL | 16708 | Hines-Pioneer-1326 138 kV line Reconductor | Replace existing 927 ACAR conductor with ACCR conductor | IL | IL | Increased reliability - This project will address congestion in the MISO RT and DA markets. |  |  |  | 2023-12-01 | 2023-12-01 | 138 | 0 | Y | 3500000 | Bottom-Up
A in MTEP20 | B>A | Central | AmerenIL | 16709 | Ashley-Venice-2: Upgrade terminal equipment at Venice Substation | Replace 2 1200A switches and 1000 Kcmil CU bus conductor with equipment having 2000A capability. Upgrade the position to 2000A. | IL | IL | Increased reliability - This project will address congestion in the MISO RT and DA markets. |  |  |  | 2021-12-01 | 2021-12-01 | 138 | 0 | Y |  | Bottom-Up
A in MTEP20 | B>A | Central | AmerenIL | 16944 | Louisville South 345-138 kV Transformer addition | Install new 345 kV ring bus at the Louisville South Substation location tapping the Newton-Xenia-1 line. Install 560 MVA 345-138 kV transformer and connect to the Louisville South 138 kV bus. | IL | IL | Increased reliabilty: Newton Unit 1 above rating with the loss of the CSYW-NWTY-1 and MTVW-XENA-4591 345 kV lines. |  |  |  | 2022-12-01 | 2022-12-01 | 345 | 138 | Y | 20000000 | Bottom-Up
A in MTEP20 | B>A | Central | AmerenIL | 16987 | Benton NW Ring bus | Install 6 position ultimate ring bus. | IL | IL | Increased reliability and operating flexibility. |  |  |  | 2023-12-01 | 2023-12-01 | 138 | 0 | Y | 8500000 | Bottom-Up
A in MTEP20 | B>A | Central | AmerenIL | 16988 | Fogarty-Limit New Line | Install new 138 kV line from Fogarty Substation to limit. Install new ring bus at Limit to make the connection | IL | IL | Increased reliability by eliminating existing radial line. |  |  |  | 2023-12-01 | 2023-12-01 | 138 | 0 | Y |  | Bottom-Up
A in MTEP20 | B>A | Central | AmerenIL | 16989 | Mattoon W Ring Bus | Install new 6 position ultimate ring bus at Mattoon West Substation. | IL | IL | Increased reliability and operating flexibility. |  |  |  | 2023-12-01 | 2023-12-01 | 138 | 0 | Y | 8500000 | Bottom-Up
A in MTEP20 | B>A | Central | AmerenIL | 16990 | Wanda Ring Bus | Install new 6 position ultimate ring bus at Wanda Substation. | IL | IL | Increased reliability and operating flexibility. |  |  |  | 2022-12-01 | 2022-12-01 | 138 | 0 | Y | 8500000 | Bottom-Up
A in MTEP20 | B>A | Central | AmerenIL | 17284 | Woodhall-Hallock 2nd circuit with Hallock ring bus | Install a second Woodhall-Hallock 138 kV line on the vacant position on the existing WDHL-HLCK-1570 circuit towers. Install 3 position initial, 6 position ultimate ring bus at Hallock Substation. | IL | IL | Hallock 138 kV bus is dropped following the outage of MOSS-HLCK-1395 & WDHL-HLCK-1570 138 kV lines, and local 69 kV bus voltage drops to 94%, 96%, and 92% in the 2019 summer peak, 2023 summer peak, and 2027 summer peak cases, respectively. The additional WDHL-HLCK 138 kV line would prevent the loss of Hallock 138 kV bus under N-2 conditions, and would keep 69 kV bus voltage at or above 100% for the same N-2 conditions. Project provides increased reliability and operating flexibility for the Peoria area. |  |  |  | 2021-12-01 | 2021-12-01 | 138 | 0 | Y | 9500000 | Bottom-Up
A in MTEP20 | B>A | Central | AmerenIL | 17285 | Quiver Substation | Install new ring bus installation at the intersection of Mason City West – Fogarty -1346 and San Jose Rail – Interstate – 1318 138 kV line. | IL | IL | Increased reliability and operating flexibility in the Mason City area. |  |  |  | 2023-12-01 | 2023-12-01 | 138 | 0 | Y | 10000000 | Bottom-Up
A in MTEP20 | B>A | Central | AmerenIL | 17324 | New Mason Ring bus for J1055 Glacier Sands interconnection | Interconncetion for new 144 MW wind farm at Mason (IL) substation. Tap existing bus at Mason to provide connection. | IL | IL | Customer requested interconnection facilities. | GIP |  |  | 2020-10-15 | 2020-10-15 | 138 | 0 | Y | 10000000 | Externally Driven
A in MTEP20 | B>A | Central | AmerenIL | 17345 | AUBN-JCKL-1306: Rebuild circuit | Scope is broken into 3 sections: o Structures 644-668 will be a complete rebuild to 1600A with 795 T2 conductor. O Structures 19-49 are single pole wood and will require structure replacements. O Jacksonville-Auburn North – 5 structure raises | IL | IL | Age and condition of existing facilities. | [5 empty] | 138 | 0 | Y |  | Bottom-Up
A in MTEP20 | B>A | Central | AmerenIL | 17565 | Orena-Decatur N 27th Street - New 138 kV line | Install new 138 kV line between Orena and Decatur N 27th Street. | IL | IL | The coincident outage of the Clinton-Brokaw-4535 345 kV line and the Latham-Oreana-4515 345 kV line would result in heavy loadings in the Decatur, IL area. For this P6-1-1 event, the ADM North-Caterpillar section of the North 27th Street Decatur-ADM North-1604 138 kV line would be loaded above its emergency rating by 8% and the North 27th Street Decatur-Caterpillar section of this same line would be loaded to its emergency rating. |  |  |  | 2025-06-01 | 2025-06-01 | 138 | 0 | Y |  | Bottom-Up
A in MTEP20 | B>A | Central | AmerenIL | 17604 | Stallings-Roxford-4581: Upgrade 345 kV switches | Upgrade 345 kV switches V4A and V4b to 3000A. Remove the 2000A wave trap. Install OPGW. | IL | IL | Increased reliability and aging infrastructure. |  |  |  | 2023-12-01 | 2023-12-01 | 345 | 0 | Y |  | Bottom-Up
A in MTEP20 | B>A | Central | AmerenIL | 17626 | Kickapoo-Limit-1325: Rebuild line | Rebuild line from Kickapoo to Limit to 2000A. Double circuit from Limit to McGrath to supply McGrath radially from Limit. | IL | IL | Increased reliability as well as age and condition of existing facilities. |  |  |  | 2024-12-01 | 2024-12-01 | 138 | 0 | Y |  | Bottom-Up
A in MTEP20 | B>A | Central | AmerenIL | 17627 | Fogarty-Kickapoo-1672: Rebuild line | Rebuild 138 kV line to 2000A | IL | IL | Age and condition of existing facilities |  |  |  | 2025-06-01 | 2025-06-01 | 138 | 0 | Y | 7500000 | Bottom-Up
A in MTEP20 | B>A | Central | AmerenIL | 17644 | Decatur Route 51 138 kV Station: Install ring bus | Install initial 138 kV 4-position (ultimate 6-position) ring bus at the Decatur Route 51 substation locattion | IL | IL | Increased reliability and operating flexibility. |  |  |  | 2022-12-01 | 2022-12-01 | 138 | 0 | Y |  | Bottom-Up
A in MTEP20 | B>A | Central | AmerenIL | 17825 | Lawrenceville South Ring Bus | Reconfigure the Lawrenceville South substation to a 6-position ultimate ring bus. | IL | IL | Aging infrastructure and increased reliability. |  |  |  | 2023-12-01 | 2023-12-01 | 138 | 0 | Y |  | Bottom-Up
A in MTEP20 | B>A | Central | AmerenIL | 17826 | GRMC-SCNT-1419 - Replace Shield wire | Replace ~22 miles of existing 5/16" HS Steel Shield Wire with 1 3/8" E.H.S. Steel Shield Wire and 1 OPGW | IL | IL | Age and condition of existing equipment. |  |  |  | 2022-12-01 | 2022-12-01 | 138 | 0 | Y |  | Bottom-Up
A in MTEP20 | B>A | Central | AmerenIL | 17827 | CTHL-STLG-1622 - Replace Shield Wire | Replace ~4 miles of existing 3 #7 Copperweld shield wire from Str. 51-Wanda Sub | IL | IL | Age and condition of existing equipment. |  |  |  | 2022-12-01 | 2022-12-01 | 138 | 0 | Y |  | Bottom-Up
A in MTEP20 | B>A | Central | AmerenIL | 17828 | KREN-PTRD-1432 - Replace Shield Wire | Replace ~6 miles of existing 3 #7 Copperweld shield wire for the entire line. | IL | IL | Age and condition of existing equipment. |  |  |  | 2022-12-01 | 2022-12-01 | 138 | 0 | Y |  | Bottom-Up
A in MTEP20 | B>A | Central | AmerenIL | 17864 | Cahokia Breaker Replacement | Replace OCB H27 on the C-GRAT-3 position and OCB H35 on the C-RUSL-2 positon with symmetrically rated SF6 55 kA circuit breakers. | IL | IL | General system expansion has increased the fault duty on these breakers, necessitating their replacement. |  |  |  | 2022-12-01 | 2022-12-01 | 138 | 0 | Y |  | Bottom-Up
A in MTEP20 | B>A | Central | AmerenIL | 17866 | Neoga Breaker Replacement | Replace OCB 1402 on the HUTY-NEGS-1 position with a symmetrically rated 40 kA SF6 breaker. | IL | IL | General system expansion has increased the fault duty on these breakers, necessitating their replacement. |  |  |  | 2022-12-01 | 2022-12-01 | 138 | 0 | Y |  | Bottom-Up
A in MTEP20 | B>A | Central | AmerenIL | 17904 | Highland Area Ring bus & 138 kV line to Aviston | Install new Highland area ring bus. Re-configure Aviston Substation to a ring bus. Install new 16.5 mile 138 kV line between Highland and Aviston. | IL | IL | Increased reliability and local load serving needs. |  |  |  | 2023-12-01 | 2023-12-01 | 138 | 0 | Y |  | Bottom-Up
A in MTEP20 | B>A | Central | AmerenIL | 17906 | HULL-MRN-1690 - Rebuild Line | Rebuild the ~7 Mile Hull-Marion-1690 161 kV line (Including Mississippi River Crossing) | IL | IL | Age and condition of existing facilities. |  |  |  | 2023-12-01 | 2023-12-01 | 161 | 0 | Y |  | Bottom-Up
A in MTEP20 | B>A | Central | AmerenIL | 17907 | Prairie Wolf Solar Farm (J949) interconnection | Add terminal facilities including one 138 kV breaker at Kansas Substation. | IL | IL | Interconnection facilities for the J949 solar farm | GIP |  |  | 2020-10-02 | 2020-10-02 | 138 | 0 | Y |  | Externally Driven
A in MTEP20 | B>A | Central | AmerenIL | 17910 | GDTY-CDNW-WFRK - Rebuild Line | Rebuild ~36 miles of the Grand Tower-Carbondale NW-W. Frankfort 138 kV line as double circuit 345/138 kV. | IL | IL | Age and condition of existing facilities as well as increased reliability. |  |  |  | 2024-12-01 | 2024-12-01 | 345 | 138 | Y |  | Bottom-Up
A in MTEP20 | B>A | Central | AmerenIL | 17972 | Salem West Ring Bus | Rebuild the Salem West 138 kV substation to a ring bus configuration. | IL | IL | Increased reliability and operating flexibility. |  |  |  | 2023-12-01 | 2023-12-01 | 138 | 0 | Y | 7000000 | Bottom-Up
A in MTEP20 | B>A | Central | AmerenIL | 17973 | Centerville Ring Bus | Rebuild the Centerville 138 kV substation to a Ring bus configuration. | IL | IL | Increased reliability and operating flexibility. |  |  |  | 2023-12-01 | 2023-12-01 | 138 | 0 | Y | 8000000 | Bottom-Up
A in MTEP20 | B>A | Central | AmerenIL | 17974 | Crab Orchard: Install 345-138 kV transformer | Tap the Shawnee-West Frankfort east-4564 line and install 345kV ring bus to make a connection for the installation of a new 345-138 kV transformer. | IL | IL | Increased reliability and system strength. |  |  |  | 2023-12-01 | 2023-12-01 | 138 | 0 | Y | 25000000 | Bottom-Up
A in MTEP20 | B>A | Central | AmerenIL | 17975 | Rising: Install 2nd 345-138 kV transformer | Install 2nd 345-138 kV transformer at Rising Substation | IL | IL | Increased reliability and system strength. |  |  |  | 2019-09-06 | 2019-09-06 | 345 | 138 | Y | 10000000 | Bottom-Up
A in MTEP20 | B>A | Central | AmerenIL | 17976 | Redhawk: Install 345-138 kV transformer | Tap the Coffeen-Roxford-4551 line and install 345kV ring bus to make the connection for a new 345-138 kV transformer at Redhawk Substation. | IL | IL | Increased reliability and system strength. |  |  |  | 2023-12-01 | 2023-12-01 | 345 | 138 | Y | 20000000 | Bottom-Up
A in MTEP20 | B>A | Central | AmerenIL | 17977 | Mt. Vernon West: Install 2nd 345-138 kV transfomer | Install 2nd 345-138 kV transformer at Mt. Vernon West Substation | IL | IL | Increased reliability and system strength |  |  |  | 2023-06-01 | 2023-06-01 | 345 | 138 | Y | 8000000 | Bottom-Up
A in MTEP20 | B>A | Central | AmerenIL | 17978 | Belleville 17th Street Ring Bus | Rebuild the Belleville 17th street 138 kV substation to a ring bus configuration. | IL | IL | Increased reliability and operating flexibility. |  |  |  | 2022-12-01 | 2022-12-01 | 138 | 0 | Y | 10000000 | Bottom-Up
A in MTEP20 | B>A | Central | AmerenIL | 17979 | North Staunton Ring Bus | Rebuild the North Stauton 138 kV substation to a ring bus configuration. | IL | IL | Increased reliability and operating flexibility. |  |  |  | 2022-06-01 | 2022-06-01 | 138 | 0 | Y | 8000000 | Bottom-Up
A in MTEP20 | B>A | Central | AmerenIL | 17981 | North Champaign Ring Bus | Rebuild the North Champaign 138 kV substation to a ring bus configuration. | IL | IL | Increased reliability and operating flexibility. |  |  |  | 2023-12-01 | 2023-12-01 | 138 | 0 | Y | 8500000 | Bottom-Up
A in MTEP20 | B>A | Central | AmerenIL | 17982 | Maroa Ring Bus | Install new Maroa 345 kV ring bus substation. | IL | IL | Increased reliability and operating flexibility. |  |  |  | 2023-12-01 | 2023-12-01 | 345 | 0 | Y | 12000000 | Bottom-Up
A in MTEP20 | B>A | Central | AmerenIL | 17983 | South Belleville Ring Bus | Rebuild the South Belleville 138 kV substation to a ring bus configuration. | IL | IL | Increased reliability and operating flexibility. |  |  |  | 2023-06-01 | 2023-06-01 | 138 | 0 | Y | 8000000 | Bottom-Up
A in MTEP20 | B>A | Central | AmerenIL | 18030 | Meredosia shunt reactive device | Install a shunt Reactive device to control voltages at IL-Meredosia 345 kV. | IL | IL | Control local area voltages during various loading conditions. |  |  |  | 2022-12-01 | 2022-12-01 | 138 | 0 | Y |  | Bottom-Up
A in MTEP20 | B>A | Central | AmerenIL | 18031 | Ipava shunt Reactive device | Install a shunt Reactive device to control voltages at Ipava 345 kV | IL | IL | Control local area voltages during various loading conditions. |  |  |  | 2023-12-01 | 2023-12-01 | 345 | 0 | Y |  | Bottom-Up
A in MTEP20 | B>A | Central | AmerenIL | 18032 | Xenia shunt Reactive device | Install a shunt Reactive device to control voltages at Xenia 345 kV | IL | IL | Control local area voltages during various loading conditions. |  |  |  | 2023-06-01 | 2023-06-01 | 138 | 0 | Y |  | Bottom-Up
A in MTEP20 | B>A | Central | AmerenIL | 18034 | Tazewell Breaker Replacements | Replace 14 138 kV breakers at Tazewell Substation including: TAZW-138KV BKR 1321-73, TAZW-138KV BKR 1340, TAZW-138KV BKR 1354, TAZW-138KV BKR 1323, TAZW-138KV BKR 1340-63 (TIE), TAZW-138KV BKR 1350 (XFMR 2), TAZW-138KV BKR 1363, TAZW-138KV BKR 1375, TAZW-138KV BKR 1353, TAZW-138KV BKR 1322, TAZW-138KV BKR 1367, TAZW-138KV BKR 1375-53, TAZW-138KV BKR 1327, TAZW-138KV BKR 1321 (XFMR 1) | IL | IL | Age and condition of existing facilities. |  |  |  | 2022-12-01 | 2022-12-01 | 138 | 0 | Y | 5600000 | Bottom-Up
A in MTEP20 | B>A | Central | AmerenIL | 18035 | Eastern Breaker Replacement | Replace TAZW-138KV BKR 1321-73 at Eastern Substation | IL | IL | Age and condition of existing facilities |  |  |  | 2022-12-01 | 2022-12-01 | 138 | 0 | Y | 500000 | Bottom-Up
A in MTEP20 | B>A | Central | AmerenIL | 18036 | Pioneer Breaker Replacement | Replace breaker PION-138KV LINE 1326 at Pioneer Substation. | IL | IL | Age and condition of existing facilities |  |  |  | 2022-12-01 | 2022-12-01 | 138 | 0 | Y | 500000 | Bottom-Up
A in MTEP20 | B>A | Central | AmerenIL | 18037 | Decatur N 27th Street Breaker Replacements | Replace breakers N27D-138KV BKR 1522 and N27D-138KV BKR 1602 at Decatur North 27th street. | IL | IL | Age and condition of existing facilities. |  |  |  | 2022-12-01 | 2022-12-01 | 138 | 0 | Y | 800000 | Bottom-Up
A in MTEP20 | B>A | Central | AmerenIL | 18039 | Havana Breaker Replacements | Replace breakers HAV-138KV BKR 1406, HAV-138KV BT BKR 1302 and HAV-138KV BKR 1422 at Havana Substation. | IL | IL | Age and condition of existing facilities |  |  |  | 2022-12-01 | 2022-12-01 | 138 | 0 | Y | 1200000 | Bottom-Up
A in MTEP20 | B>A | Central | AmerenIL | 18041 | Ottawa 138kV Line Breaker | Install new line breaker on the HENN-OGLE-1516 line at Ottawa Substation. | IL | IL | Increased reliability and operating flexibility. |  |  |  | 2022-12-01 | 2022-12-01 | 138 | 0 | Y | 2000000 | Bottom-Up
A in MTEP20 | B>A | Central | AmerenIL | 18042 | Wedron Fox River 138kV Line Breaker | Install new line breaker on the OTTA-FOXR-1652 circuit at Wedron Fox River Substation. | IL | IL | Increased reliability and operating flexibility. |  |  |  | 2022-12-01 | 2022-12-01 | 138 | 0 | Y | 2000000 | Bottom-Up
A in MTEP20 | B>A | Central | AmerenIL | 18044 | Caterpillar quad circuit replacement | Reconfigure the Tazewell-Caterpillar 2-1375, Edwards-Caterpillar 1-1374, RS Wallace-Keystone-1396 and the Caterpillar 2-Hines-1357 138 kV circuits on a 1.5 mile section where they share a common structure. | IL | IL | Increased reliability and operating flexibility. The Tazewell-Caterpillar 2-1375, Edwards-Caterpillar 1-1374, RS Wallace-Keystone-1396 and the Caterpillar 2-Hines-1357 138 kV circuits are all attached to common towers in this 1.5 mile section, which makes maintenance work on these lines extremely difficult and provides a single mode of failure to CAT1 and CAT2 subs. |  |  |  | 2024-12-01 | 2024-12-01 | 138 | 0 | Y | 5000000 | Bottom-Up
A in MTEP20 | B>A | Central | AmerenIL | 18045 | Murdock Circuit Switcher installation | Install a 138 kV circuit switcher on the high-side of XFMR #1 at Murdock Substation. | IL | IL | Increased reliability and operating flexibility. |  |  |  | 2023-06-01 | 2023-06-01 | 138 | 0 | Y | 1000000 | Bottom-Up
A in MTEP20 | B>A | Central | AmerenIL | 18054 | Norris City shunt reactive device | Install a shunt Reactive device to control voltages at Norris City 345 kV | IL | IL | Control local area voltages during various loading conditions. |  |  |  | 2023-06-01 | 2023-06-01 | 345 | 0 | Y |  | Bottom-Up
A in MTEP20 | B>A | Central | AmerenIL | 18057 | WWSH-HUFF-1364: Upgrade terminal equipment | Upgrade W. Washington 1200 A wave trap and Diamond Star Tap 1200 A switch. | IL | IL | 105.72% loading 2024 Summer peak based on 2019 analysis with N-1-1 outage of MCLEAN:BROKAW:8001 and PONTIAC:BLUEMOUND:L8002. |  |  |  | 2024-06-01 | 2024-06-01 | 138 | 0 | Y |  | Bottom-Up
A in MTEP20 | B>A | Central | AmerenIL | 18059 | Louisville-Jasper: Replace switch | Replace limiting switch 1602L at Louisville with 2000A switch | IL | IL | 104% loading 2024 Summer peak based on 2019 analysis with N-1-1 outage of MTVERNON-W:XENIA:1 and P12:345:AMIL::CASEYWEST:NEWTON:1. |  |  |  | 2024-06-01 | 2024-06-01 | 138 | 0 | Y |  | Bottom-Up
A in MTEP20 | B>A | Central | AmerenIL | 18075 | North Decatur Breaker Replacement | Replace 138 kV breaker NDEC-138KV BKR 1602 at North Decatur Substation. | IL | IL | Age and condition of existing facilities |  |  |  | 2023-12-01 | 2023-12-01 | 138 | 0 | Y | 500000 | Bottom-Up
A in MTEP20 | B>A | Central | AmerenIL | 18076 | Steeleville Breaker Replacement | Replace 138 kV breaker STVL-138KV BKR 1636 at Steeleville Substation. | IL | IL | Age and condition of existing facilities |  |  |  | 2023-12-01 | 2023-12-01 | 138 | 0 | Y | 500000 | Bottom-Up
A in MTEP20 | B>A | Central | AmerenIL | 18077 | Vermilion Switchyard Breaker Replacement | Replace 138 kV breaker VERM-138KV BKR 1306 at Vermilion Substation. | IL | IL | Age and condition of existing facilities |  |  |  | 2023-12-01 | 2023-12-01 | 138 | 0 | Y | 500000 | Bottom-Up
A in MTEP20 | B>A | Central | AmerenIL | 18078 | Carbondale NW Breaker Replacement | Replace 138 kV breaker CDNW-138KV LINE 1744 at Carbondale NW Substation. | IL | IL | Age and condition of existing facilities |  |  |  | 2023-12-01 | 2023-12-01 | 138 | 0 | Y | 500000 | Bottom-Up
A in MTEP20 | B>A | Central | AmerenIL | 18079 | Mason City W Breaker Replacement | Replace 138 kV breaker MSCW-138KV LINE 1684 at Mason City West substation. | IL | IL | Age and condition of existing facilities |  |  |  | 2023-12-01 | 2023-12-01 | 138 | 0 | Y | 500000 | Bottom-Up
A in MTEP20 | B>A | Central | AmerenIL | 18080 | Meredosia E Breaker Replacements | Replace breakers MERE-138KV BT 1938, MERE-138KV BT 1958, MERE-138KV BKR 1957, MERE-138KV BKR 1947 and MERE-138KV BT 1948 at Meredosia East Substation. | IL | IL | Age and condition of existing facilities |  |  |  | 2023-12-01 | 2023-12-01 | 138 | 0 | Y | 2000000 | Bottom-Up
A in MTEP20 | B>A | Central | AmerenIL | 18081 | Newton Switchyard Breaker Replacements | Replace 138 kV breakers NWTY-138KV LT 1869 and NWTY-138KV LT 1868 at the Newton switchyard. | IL | IL | Age and condition of existing facilities |  |  |  | 2023-12-01 | 2023-12-01 | 138 | 0 | Y | 800000 | Bottom-Up
A in MTEP20 | B>A | Central | AmerenIL | 18085 | Tazewell XFMR 1 Replacement | Replace 345-138 kV transformer with new 560 MVA unit. | IL | IL | Age and condition of existing facilities |  |  |  | 2022-06-01 | 2022-06-01 | 345 | 138 | Y | 3750000 | Bottom-Up
A in MTEP20 | B>A | Central | AmerenIL | 18086 | Tazewell XFMR 2 Replacement | Replace 345-138 kV transformer with new 560 MVA unit. | IL | IL | Age and condition of existing facilities |  |  |  | 2024-06-01 | 2024-06-01 | 345 | 138 | Y | 3750000 | Bottom-Up
A in MTEP20 | B>A | Central | AmerenIL | 18087 | Norris City N XFMR 2 Replacement | Replace 345-138 kV transformer with new 560 MVA unit. | IL | IL | Age and condition of existing facilities |  |  |  | 2022-12-01 | 2022-12-01 | 345 | 138 | Y | 3750000 | Bottom-Up
A in MTEP20 | B>A | Central | AmerenIL | 18088 | Neoga South XFMR 2 Replacement | Replace 345-138 kV transformer with new 560 MVA unit. | IL | IL | Age and condition of existing facilities |  |  |  | 2023-06-01 | 2023-06-01 | 345 | 138 | Y | 3750000 | Bottom-Up
A in MTEP20 | B>A | Central | AmerenIL | 18089 | Brokaw XFMR 1 Replacement | Replace 345-138 kV transformer with new 560 MVA unit. | IL | IL | Age and condition of existing facilities |  |  |  | 2023-12-01 | 2023-12-01 | 345 | 138 | Y | 3750000 | Bottom-Up
A in MTEP20 | B>A | Central | AmerenIL | 18090 | Albion South XFMR 3 Replacement | Replace 345-138 kV transformer with new 560 MVA unit. | IL | IL | Age and condition of existing facilities |  |  |  | 2024-12-01 | 2024-12-01 | 345 | 138 | Y | 3750000 | Bottom-Up
A in MTEP20 | B>A | Central | AmerenIL | 18091 | Clinton Breaker Replacement | Replace breaker CLNT-345KV BKR 4506 at Clinton switchyard. | IL | IL | Age and condition of existing facilities |  |  |  | 2023-12-02 | 2023-12-02 | 345 | 0 | Y | 500000 | Bottom-Up
A in MTEP20 | B>A | Central | AmerenIL | 18092 | East Galesburg Transformer Breaker Replacement | Replace breaker EGAL-138/69KV AUTO XFMR 2 at East Galesburg Substation. | IL | IL | Age and condition of existing facilities |  |  |  | 2024-12-01 | 2024-12-01 | 138 | 0 | Y | 500000 | Bottom-Up
A in MTEP20 | B>A | Central | AmerenIL | 18093 | Fargo Breaker Replacements | Replace breakers FARG-138KV BKR & LINE 1394 and FARG-138KV BKR 1371 at Fargo Substation. | IL | IL | Age and condition of existing facilities |  |  |  | 2024-12-01 | 2024-12-01 | 138 | 0 | Y | 800000 | Bottom-Up
A in MTEP20 | B>A | Central | AmerenIL | 18095 | Gibson City S Breaker Replacements | Replace breakers GBCS-138KV LINE 1524 and GBCS-138KV LINE 1522 at Gibson City South Substation. | IL | IL | Age and condition of existing facilities |  |  |  | 2024-12-01 | 2024-12-01 | 138 | 0 | Y | 800000 | Bottom-Up
A in MTEP20 | B>A | Central | AmerenIL | 18096 | Goose Creek Breaker Replacements | Replace breakers GOSC-345KV BKR 4545, GOSC-345KV BKR 4575 and GOSC-345KV LT BKR 4555 at Goose Creek Substation. | IL | IL | Age and condition of existing facilities |  |  |  | 2023-12-01 | 2023-12-01 | 345 | 0 | Y | 1800000 | Bottom-Up
A in MTEP20 | B>A | Central | AmerenIL | 18098 | Grand Tower Breaker Replacement | Replace breaker GDTY-138KV LT 1449 at Grand Tower Switchyard. | IL | IL | Age and condition of existing facilities |  |  |  | 2024-12-01 | 2024-12-01 | 138 | 0 | Y | 500000 | Bottom-Up
A in MTEP20 | B>A | Central | AmerenIL | 18102 | Hines Breaker Replacement | Replace breaker HINE-138KV BKR & LINE 1357 at Hines Substation. | IL | IL | Age and condition of existing facilities |  |  |  | 2023-12-01 | 2023-12-01 | 138 | 0 | Y | 500000 | Bottom-Up
A in MTEP20 | B>A | Central | AmerenIL | 18104 | Latham Breaker Replacement | Replace breaker LATM-345KV POS V19 at Latham Substation. | IL | IL | Age and condition of existing facilities |  |  |  | 2023-12-01 | 2023-12-01 | 345 | 0 | Y | 500000 | Bottom-Up
A in MTEP20 | B>A | Central | AmerenIL | 18105 | Makanda N Breaker Replacements | Replace breakers MAKN-138KV LINE 1674 and MAKN-138KV LINE 1672 at Makanda North Substation. | IL | IL | Age and condition of existing facilities |  |  |  | 2024-06-01 | 2024-06-01 | 138 | 0 | Y | 800000 | Bottom-Up
A in MTEP20 | B>A | Central | AmerenIL | 18106 | Marblehead N Breaker Replacements | Replace breakers MRBN-138KV LINE 1852 and MRBN-161/138KV XFMR 1 at Marblehead north substation. | IL | IL | Age and condition of existing facilities |  |  |  | 2024-06-01 | 2024-06-01 | 161 | 138 | Y | 800000 | Bottom-Up
A in MTEP20 | B>A | Central | AmerenIL | 18107 | Tilton Energy Center Breaker Replacement | Replace breaker TEC-138KV LINE TIE BKR 1320 at Tilton Energy Center. | IL | IL | Age and condition of existing facilities |  |  |  | 2023-12-01 | 2023-12-01 | 138 | 0 | Y | 500000 | Bottom-Up
A in MTEP20 | B>A | Central | AmerenIL | 18108 | Watseka Breaker Replacements | Replace breakers WATK-138KV LINE 1372 and WATK-138KV LINE 1374 at Watseka Substation. | IL | IL | Age and condition of existing facilities |  |  |  | 2024-12-01 | 2024-12-01 | 138 | 0 | Y | 800000 | Bottom-Up
A in MTEP20 | B>A | Central | AmerenIL | 18249 | Corbin Battery Installation | Install a 125 MVA battery system with a four quadrant inverter. The inverter should be capable of producing 100 MW for four hours. | IL | IL | The battery at Corbin will provide support to the LaSalle and Bureau counties for several different 138 kV N-1-1 contingencies. |  |  |  | 2022-06-01 | 2022-06-01 | 138 | 0 | Y |  | Bottom-Up
A in MTEP20 | B>A | Central | AmerenIL | 18250 | Robinson Area Battery Installation | Install an 80 MVA battery system with a four quadrant inverter at a new substation just south of Robinson Marathon. The battery should be capable of producing 40 MW for 4 hours. Re locate the Robinson – Newton 138 kV line and the Robinson – Lawrenceville 138 kV line in and out of the new substation. | IL | IL | The battery at Robinson will provide voltage support to a soft spot on the system for the loss of the Newton – Robinson 138 kV line paired with another 138 kV contingency. |  |  |  | 2022-06-01 | 2022-06-01 | 138 | 0 | Y |  | Bottom-Up
A in MTEP20 | B>A | Central | AmerenIL | 18263 | Fargo – Hines 138 kV line | Construct a new line between the Fargo 138 kV substation and the Hines 138 kV substation. | IL | IL | This line is to prevent over 300 MW of load from being dropped for the loss of the Fargo – Radnor 138 kV line and the Tazewell to Cat2 138 kV line per Ameren Local Planning Criteria. |  |  |  | 2025-06-01 | 2025-06-01 | 138 | 0 | Y |  | Bottom-Up
A in MTEP20 | B>A | Central | AmerenIL | 18269 | LaSalle – North Utica (Area) 138 kV line | Construct a new 138 kV ring bus breaking the North Lassalle – Fox River 138 kV line. Construct a new line between LaSalle 138 kV substation and new ring bus. Add two line breaker at the LaSalle 138 kV substation. | IL | IL | This line is to prevent over 300 MW of load from being dropped for the loss of several 138 kV N-1-1 contingency pairs. |  |  |  | 2025-06-01 | 2025-06-01 | 138 | 0 | Y |  | Bottom-Up
A in MTEP20 | B>A | Central | AmerenIL | 18275 | Holland Northwest-Neoga South-4509 345 kV Line | Construct a 345 kV double circuit on the exisitng Holland Northwest-Neoga South-4509 line R.O.W. replacing structures. Target rating: 3000 A summer emergency. | IL | IL | N-1-1: the Pana-Ramsey, East-1 138 kV line could be loaded to its rating during Summer peak should the existing Holland-Neoga and Ramsey-Coffeen 345 kV lines be outaged, |  |  |  | 2023-12-01 | 2023-12-01 | 345 | 0 | Y |  | Bottom-Up
A in MTEP20 | B>A | Central | AmerenIL | 18279 | South Ottawa Breaker addition | Install 138 kV bus-tie breaker at the switch 1516 position at South Ottawa | IL | IL | Increased reliability: 32 Mvar cap bank will remain in service with loss of south end of the HENN-OGLE-1516 line relieving voltage concerns in the area. |  |  |  | 2022-12-01 | 2022-12-01 | 138 | 0 | Y |  | Bottom-Up
A in MTEP20 | B>A | Central | AmerenIL | 18310 | J811 Dressor Plains Solar Generator interconnection | Add terminal facilities to Ramsey East Substation. | IL | IL | Generator Interconnection | GIP |  |  | 2020-09-01 | 2020-09-01 | 138 | 0 | Y |  | Externally Driven
A in MTEP20 | B>A | Central | AmerenIL | 18311 | J813 Maple Flats Solar Generator Interconnection | Re-configure Louisville South 138 kV substation to ring bus. Add terminal facilities for J813 connection. | IL | IL | Generator Interconnection. | GIP |  |  | 2020-09-30 | 2020-09-30 | 138 | 0 | Y |  | Externally Driven
A in MTEP20 | B>A | Central | AmerenIL | 18314 | J826 McLean County Wind Generator Interconnection | Add breaker position to existing ring bus at Weedman Substation for the J826 interconnection. | IL | IL | Generator Interconnection | GIP |  |  | 2020-09-01 | 2020-09-01 | 138 | 0 | Y |  | Externally Driven
A in MTEP20 | B>A | Central | AmerenIL | 18315 | J844 Galesburg Wind Generator Interconnection | Add 1 BAAH 138 kV leg to the Sandburg Substation and add 1 breaker postion to interconnect J844. | IL | IL | Generator Interconnection | GIP |  |  | 2020-09-10 | 2020-09-10 | 138 | 0 | Y |  | Externally Driven
A in MTEP20 | B>A | Central | AmerenIL | 18316 | J853 Big River Solar Generator interconnection | Add terminal facilities to the Norris City North 138 kV bus to interconnect J853. | IL | IL | Generator Interconnection | GIP |  |  | 2020-09-01 | 2020-09-01 | 138 | 0 | Y |  | Externally Driven
A in MTEP20 | B>A | Central | AmerenIL | 18317 | J884 Brokaw Solar Generator Interconnection | Expand Brokaw 138 kV bus and add a breaker postion for the J884 interconnection. | IL | IL | Generator Interconnection | GIP |  |  | 2020-09-15 | 2020-09-15 | 138 | 0 | Y |  | Externally Driven
A in MTEP20 | B>A | Central | AmerenIL | 18320 | J715 Bennington Wind Generator interconnection | Install new 138 kV ring bus on the McLean-Oglesby line to make the interconnection for J715. | IL | IL | Generator Interconnection | GIP |  |  | 2020-06-01 | 2020-06-01 | 138 | 0 | Y |  | Externally Driven
A in MTEP20 | B>A | Central | AmerenIL | 18321 | J845 Ford County Wind Generator Interconnection | Install new ring bus on the Gibson City South-Paxton East 138 kV line to make the interconnection for J845. | IL | IL | Generator Interconnection | GIP |  |  | 2020-06-01 | 2020-06-01 | 138 | 0 | Y |  | Externally Driven
A in MTEP20 | B>A | Central | AmerenIL | 18322 | J848 City of Roses Wind Generator Interconnection | Add terminal facilities at the Pana 138 kV Substation to make the inteconnection for J848. | IL | IL | Generator Interconnection | GIP |  |  | 2020-09-30 | 2020-09-30 | 138 | 0 | Y |  | Externally Driven
A in MTEP20 | B>A | Central | AmerenIL | 18323 | J859 Cass County Solar Generator Interconnection | Install a new ring bus on the Meredosia East-Ipava South 138 kV line to make the interconnection for J859. | IL | IL | Generator Interconnection | GIP |  |  | 2020-09-01 | 2020-09-01 | 138 | 0 | Y |  | Externally Driven
A in MTEP20 | B>A | Central | AmerenIL, AmerenMO | 17905 | Hannibal Area ring bus and Hull Transformer Addition | Install new 161 kV Hannibal area ring bus. Convert the Spalding Substation to a ring bus configuration adding a positon for a line to the Hannibal area Substation. Double circuit the PENO-SPLD-2 line from Spalding to the Marion tap and rebuild the Marion Tap 161 kV section of the PENO-SPLD-2 line to the Mississippi River, through the new Hannibal area Substation and the existing Marion Substation. Install new 161 kV bus-tie breaker at Marion Substation. Install new 161-138 kV transformer at Hull substation. Operate the HULL-MRN-1690 line at 161kV. | MO | IL | Increased reliability, local load serving needs and age and condition of existing facilities. |  |  |  | 2022-06-01 | 2023-06-01 | 161 | 138 | Y |  | Bottom-Up
A in MTEP20 | B>A | Central | CWLP | 18134 | Add Cap Banks - Palomino | Add two (2) 20 MVAR capacitor banks to the Palomino substation. In adding two capacitor banks to the Palomino substation, we will also be retiring the existing cap bank at Palomino. | IL | IL | With the potential retirement of coal fired units Dallman 31, Dallman 32, and Dallman 33, CWLP will need to add capacitor banks to the CWLP system in order to provide voltage support under certain contingency scenarios. |  |  |  | 2021-03-01 | 2021-03-01 | 69 | 0 | Y | 250000 | Bottom-Up
A in MTEP20 | B>A | Central | CWLP | 18140 | Reconductor Chatham Main - Chatham Independence 138 kV line | Reconductor Chatham Main - Chatham Independence 138 kV line with 795 ACSS. | IL | IL | Unit retirements will mean we will need to import more over our tie-lines. Contingencies show these lines will overload under certain import scenarios. Reconductoring the line should alleviate these concerns. |  |  |  | 2021-03-01 | 2021-03-01 | 138 | 0 | Y | 350000 | Bottom-Up
A in MTEP20 | B>A | Central | CWLP | 18141 | Interstate Sub - Replace Wavetrap | Replace the wavetrap on the Interstate - Lanesville 138 kV line (at Interstate Sub) with a 2000A wave trap. This will increase the rating of the line. | IL | IL | Retiring units will require CWLP to import more power over tie-lines. Contingencies will cause this line to overload under certain import scenarios. Upgrading the wavetrap should alleviate these concerns. |  |  |  | 2021-03-01 | 2021-03-01 | 138 | 0 | Y | 20000 | Bottom-Up
A in MTEP20 | B>A | Central | CWLP | 18143 | Reconductor Amos - Amos PPI 69 kV line | Reconductor the Amos - Amos PPI 69 kV line with 397 ACSR | IL | IL | Retiring units will require CWLP to import more over their tie-lines. Contingencies will cause this line to overload under certain import scenarios. Reconductoring the line should alleviate these concerns. |  |  |  | 2021-03-01 | 2021-03-01 | 69 | 0 | Y | 10000 | Bottom-Up
A in MTEP20 | B>A | Central | CWLP | 18171 | Reconductor Chatham Independence - Spaulding 138 kV line | Reconductor Chatham Ind. - Spaulding 138 kV line with 795 ACSS. | IL | IL | Unit retirements mean we will import more over our lines. Contingencies can cause the line to overload under certain import scenarios. Reconductoring the line should alleviate these issues |  |  |  | 2021-03-01 | 2021-03-01 | 138 | 0 | Y | 150000 | Bottom-Up
A in MTEP20 | B>A | Central | CWLP | 18172 | Add Cap Banks - Taintor | Add two (2) 20 MVAR capacitor banks at Taintor Substation | IL | IL | Unit retirements will require additional cap banks for voltage support |  |  |  | 2021-03-01 | 2021-03-01 | 69 | 0 | Y | 250000 | Bottom-Up
A in MTEP20 | B>A | West | ITCM | 17725 | Savanna 161kV Substation Expansion | TC will be expanding the Savanna Substation to a Ring Bus capable of 6-positions. The new 161kV equipment will be capable of 2000A. There will be several phases for the 161kV. | IL | IL | Age and condition of the 34kV system. Contractual obligations to convert 34kV to 69kV networked system. |  |  |  | 2021-12-31 | 2021-12-31 | 161 | 161 | Y |  | Bottom-Up
A in MTEP20 | B>A | West | ITCM | 17726 | Savanna 69kV Substation Expansion | ITC will be expanding the Savanna 69kV Substation to a Ring Bus capable of 6-positions. Most new 69kV equipment will be capable of 1200A or greater. ITC will install a 161/69kV 150MVA transformer at Savanna. The 161/69kV transformer position and the Metform position will be capable of 2000A or greater. There will be several phases for the 69kV. | IL | IL | Age and condition of the 34kV system. Contractual obligations to convert 34kV to 69kV networked system. |  |  |  | 2021-12-31 | 2021-12-31 | 69 | 69 | Y |  | Bottom-Up
A in MTEP20 | B>A | West | ITCM | 17727 | York Substation 69kV Expansion | ITC will be expanding the York Substation to include a 161/69kV 150MVA transformer. All new 69kV equipment will be capable of 2000A. A tie switch will be added to the 161kV. All new 161kV equipment will be capable of 2000A or greater. See page 2 for the electrical layout of the York Substation. ITC will be retiring the 34.5kV out of the York Substation. No additional 161kV equipment will be needed to accommodate this work. All new 69kV equipment will be capable of 1200A or greater. | IL | IL | Age and condition of the 34kV system. Contractual obligations to convert 34kV to 69kV networked system. |  |  |  | 2021-12-31 | 2025-12-30 | 69 | 69 | Y |  | Bottom-Up
A in MTEP20 | B>A | West | ITCM | 17728 | Savanna-Metform-York 34kV to 69kV Rebuild | ITC will rebuild approximately 6 miles of the Savanna – Metform – York 34.5kV line to 69kV standards. The overhead conductor will have an ampacity of 1200A or higher. ITC will need to investigate the Danisco to York 34.5kV to determine if the insulators are capable of 69kV operation. If not, ITC will reinsulate the Danisco to York 34.5kV line with 69kV insulators. The existing conductor is 954 ACSR and does not need to be replaced due to ampacity needs. The static is 3/8 steel. | IL | IL | Age and condition of the 34kV system. Contractual obligations to convert 34kV to 69kV networked system. |  |  |  | 2020-12-30 | 2020-12-30 | 69 | 69 | Y |  | Bottom-Up
A in MTEP20 | B>A | West | ITCM | 17729 | Savanna-Argo Fay-York Area Rebuilds | ITC will build a new 69kV line approximately 6 miles from the York Substation to the Argo Fay Substation. The overhead conductor will have an ampacity of 600A or higher. A route study may be needed to determine the best route. ITC will build a new 69kV line approximately 6.5 miles from the Clay Substation to the Chadwick Substation. The overhead conductor will have an ampacity of 600A or higher. A route study may be needed to determine the best route. ITC will rebuild approximately 6.5 miles of the Argo Fay Substation to the Chadwick Substation 34.5kV line to 69kV Standards. The overhead conductor will have an ampacity of 600A or higher. ITC will retire approximately 6 miles of 34.5kV line between Argo Fay and the Clay substation. ITC will retire approximately 6 miles of 34.5kV line between Argo Fay and the Savanna substation. | IL | IL | Age and condition of the 34kV system. Contractual obligations to convert 34kV to 69kV networked system. |  |  |  | 2025-12-30 | 2025-12-30 | 69 | 34 | Y |  | Bottom-Up
A in MTEP20 | B>A | West | ITCM | 17730 | Savanna-Clay 34kV to 69kV Rebuild | ITC will rebuild approximately 7.75 miles of 34.5kV to 69kV standards from Savanna Substation to Clay Substation. The overhead conductor will have an ampacity of 600A or higher. A route study may be needed to determine the best route. | IL | IL | Age and condition of the 34kV system. Contractual obligations to convert 34kV to 69kV networked system. |  |  |  | 2025-12-30 | 2025-12-30 | 69 | 69 | Y |  | Bottom-Up
A in MTEP20 | B>A | West | ITCM | 17731 | Savanna City Loop 34kV to 69kV Rebuild | ITC will rebuild approximately 1.66 miles of the Savanna – Eaton 34.5kV line to 69kV standards. The overhead conductor will have an ampacity of 600A or higher. ITC will rebuild approximately 0.85 miles of the Bowen – Eaton 34.5kV line to 69kV standards. The overhead conductor will have an ampacity of 600A or higher. ITC will rebuild approximately 3.80 miles of the Bowen – Savanna 34.5kV line to 69kV standards. The overhead conductor will have an ampacity of 600A or higher. | IL | IL | Age and condition of the 34kV system. Contractual obligations to convert 34kV to 69kV networked system. |  |  |  | 2025-12-30 | 2025-12-30 | 69 | 69 | Y |  | Bottom-Up
A in MTEP20 | B>A | West | ITCM | 17966 | Metform Substation 69kV Conversion | ITC will be converting the Metform Substation to 69kV. All network path 69kV equipment will be capable of 1200A or greater. All network path switches will need to be replaced to be capable of 1200A or greater. ITC will retire the bypass bus and switches. | IL | IL | Age and condition of the 34kV system. Contractual obligations to convert 34kV to 69kV networked system. |  |  |  | 2021-12-31 | 2021-12-31 | 69 | 69 | Y |  | Bottom-Up
A in MTEP20 | B>A | West | ITCM | 17967 | Bowen Substation 69kV Conversion | ITC will be converting the Bowen Substation to 69kV. All network path 69kV equipment will be capable of 600A or greater. | IL | IL | Age and condition of the 34kV system. Contractual obligations to convert 34kV to 69kV networked system. |  |  |  | 2029-12-30 | 2029-12-30 | 69 | 69 | Y |  | Bottom-Up
A in MTEP20 | B>A | Central | PPI | 18115 | Move Kampsville Capacitor Bank to Pearl | Move 2.4 MVAR capacitor bank from Kampsville to Pearl Substation | IL | IL | Reliability. Kampsville substation is prone to Illinois River flooding making capacitor bank unavailable |  |  |  | 2020-12-31 | 2020-12-31 | 69 | 69 | Y | 400000 | Bottom-Up
A in MTEP20 | B>A | Central | PPI | 18116 | New Saidora-Kilbourne 69 kV Line | New 9.7-mile 69 kV line in Menard Elecric Cooperative | IL | IL | Reliability. Provide new source for Saidora substation by tying into Grand Island |  |  |  | 2023-12-31 | 2023-12-31 | 69 | 69 | Y | 6195200 | Bottom-Up
A in MTEP20 | B>A | Central | PPI | 18120 | Upgrade Berlin-Amos 69 kV Line | Upgrade 3-mile portion of Berlin to Amos 69 kV line from 4/0 ACSR to 336.4 MCM ACSR associated with fiber and distribution installation | IL | IL | Age and condition |  |  |  | 2020-12-31 | 2020-12-31 | 69 | 69 | Y | 1200000 | Bottom-Up
A in MTEP20 | B>A | Central | PPI | 18122 | Replace St. David 69 kV Substation breaker | Replace St. David OCB with SF6 breaker and new relays | IL | IL | Age and condition |  |  |  | 2020-12-31 | 2020-12-31 | 69 | 69 | Y | 280000 | Bottom-Up
A in MTEP20 | B>A | Central | PPI | 18123 | New Burton Tap 69 kV Breaker Station | Establish 69 kV breaker station in Adams Electric Cooperative | IL | IL | Reliability. Sectionalize 5 substations in Adams Electric Cooperative; elliminate 3-terminal line |  |  |  | 2021-12-31 | 2021-12-31 | 69 | 69 | Y | 2940400 | Bottom-Up
A in MTEP20 | B>A | Central | PPI | 18148 | New Riggston 138 kV ring bus | Establish 138 kV ring bus to serve proposed Data Center in Illinois Electric Cooperative new load between Jacksonville Industrial Park and Winchester. | IL | IL | Load Growth. Up to 60 MW new load for proposed data center in Illinois Electric Cooperative |  |  |  | 2021-12-31 | 2021-12-31 | 138 | 138 | Y | 6400000 | Bottom-Up
A in MTEP20 | B>A | Central | PPI | 18152 | Reconductor Andrew-Amos 69 kV line | Reconductor 8.9-mile 69 kV line from 336.4 MCM ACSR to 795 MCM ACSR | IL | IL | Reliability. Increase rating from 50 MVA to 115 MVA to accommodate increased flows from Fancy Creek substation during CWLP imports. |  |  |  | 2022-12-31 | 2022-12-31 | 69 | 69 | Y | 5239200 | Bottom-Up
A in MTEP20 | B>A | Central | PPI | 18154 | New Alsey Reactor | Addition of 40 MVAR reactor at Alsey 138 kV substation | IL | IL | Baseline Reliability Project. Reduce voltage on 138 kV during low load times to meeting planning criteria |  |  |  | 2022-12-31 | 2022-12-31 | 138 | 138 | Y | 3240000 | Bottom-Up
A in MTEP20 | B>A | Central | PPI | 18155 | New Burton-Ursa 69 kV Line | New 16.3-mile 69 kV line in Adams Electric Cooperative | IL | IL | Reliablity. Convert Ursa distribution substation from 34.5 kV to 69 kV |  |  |  | 2022-12-31 | 2022-12-31 | 69 | 69 | Y | 8945250 | Bottom-Up
A in MTEP20 | B>A | Central | PPI | 18157 | New Kuhlman 138/69 kV Substation | "1) Establish 138 kV substation connecting to the Ameren Meredosia to Frederick 138 kV line 2) New PPI Kuhlman 138/69 kV substation" | IL | IL | Reliability. Provide new source for Arenzville Substation; help backup Winchester and Grand Island |  |  |  | 2022-12-31 | 2022-12-31 | 138 | 69 | Y | 7425000 | Bottom-Up
A in MTEP20 | B>A | Central | PPI | 18159 | Upgrade East Lanesville 138/69 kV transformer | Upgrade existing 37.33 MVA transformer with 84 MVA unit. Existing transformer will be moved to Kuhlman | IL | IL | Reliability. Increased capability necessary to back up Pleasant View transformer and to accomoate CWLP imports. |  |  |  | 2022-12-31 | 2022-12-31 | 138 | 69 | Y | 1200000 | Bottom-Up
A in MTEP20 | B>A | Central | PPI | 18160 | New Arenzville-Bluff Springs 69 kV Line | New 11.6-mile 69 kV line tying Illinois Electric Cooperative to Menard Electric Cooperative | IL | IL | Reliability. Provide network feed for 3 substations |  |  |  | 2023-12-31 | 2023-12-31 | 69 | 69 | Y | 7459000 | Bottom-Up
A in MTEP20 | B>A | Central | PPI | 18161 | New Bluff Springs-Virginia 69 kV Line | New 13.8-mile 69 kV line in Menard Electric Cooperative | IL | IL | Reliability. Provide new source for Virginia substation |  |  |  | 2023-12-31 | 2023-12-31 | 69 | 69 | Y | 8000000 | Bottom-Up
A in MTEP20 | B>A | Central | PPI | 18162 | New Ellisville-Kington 69 kV Line | New 12.4-mile 69 kV line in Adams Electric Cooperative | IL | IL | Reliability. Provide network feed for 4 substations |  |  |  | 2023-12-31 | 2023-12-31 | 69 | 69 | Y | 11925000 | Bottom-Up
A in MTEP20 | B>A | Central | PPI | 18163 | New Ursa-Big Neck 69 kV Line | New 12.4-mile 69 kV line in Adams Electric Cooperative | IL | IL | Reliablity. Provide network feed for Burton, Ursa, and Big Neck substations |  |  |  | 2023-12-31 | 2023-12-31 | 69 | 69 | Y | 9024000 | Bottom-Up
A in MTEP20 | B>A | Central | PPI | 18165 | New Virginia 69 kV Breaker Station | New 69 kV breaker station in Menard Electric Cooperative | IL | IL | Sectionalize 69 kV line feeding 7 substations |  |  |  | 2023-12-31 | 2023-12-31 | 69 | 69 | Y | 2929500 | Bottom-Up
A in MTEP20 | B>A | Central | PPI | 18166 | New Virginia-Saidora 69 kV Line | New 14.9-mile 69 kV line in Menard Electric Cooperative | IL | IL | Reliability. Complete network between Arenzville and Grand Island |  |  |  | 2023-12-31 | 2023-12-31 | 69 | 69 | Y | 8640000 | Bottom-Up
A in MTEP20 | B>A | Central | PPI | 18167 | New Smithfield 69 kV Breaker Station capacitor bank | Addition of 4.8 MVAR capacitor bank in Spoon Rvier Electric Cooperative | IL | IL | Reliability. Provide voltage support for high loads, switching flexibility and contingencies |  |  |  | 2024-12-31 | 2024-12-31 | 69 | 69 | Y | 400000 | Bottom-Up
A in MTEP20 | B>A | Central | PPI | 18169 | New Macomb 69 kV Breaker Station capacitor bank | Addition of 4.8 MVAR capacitor bank in McDonough Power Cooperative | IL | IL | Reliability. Provide voltage support for high loads, switching flexibility and contingencies |  |  |  | 2026-12-31 | 2026-12-31 | 69 | 69 | Y | 400000 | Bottom-Up
A in MTEP19 | B>A | Central | AmerenIL | 4483 | New Fargo 345/138 kV transformer No. 2 | Install 2nd. 345/138 kV, 560 MVA Transformer | IL | IL | Required due to anticipated retirement of coal units in the area. | Other |  | Reliability | 2021-06-01 | 2021-06-01 | 345 | 138 | Y | 8000000 | Bottom-Up
A in MTEP19 | B>A | Central | AmerenIL | 7826 | Reconfigure Turkey Hill 138 kV into Ring Bus | Convert existing 138 kV straight bus to a ring bus. Initial 4 positions with an ultimate of 6 positions. | IL | IL | Increased reliability | Other |  | Reliability | 2019-12-01 | 2019-12-01 | 138 | 0 | Y | 7500000 | Bottom-Up
A in MTEP19 | B>A | Central | AmerenIL | 7863 | Reconfigure Prest (FormerlyTilden) 138 kV Substation into a Ring Bus | Establish a 5 position 138 kV ring bus for 4-138 kV lines and 1-138/34.5 kV transformer. | IL | IL | Increased reliability | Other |  | Reliability | 2018-12-01 | 2018-12-01 | 138 | 0 | Y | 11100000 | Bottom-Up
A in MTEP19 | B>A | Central | AmerenIL | 9729 | Upgrade North Decatur-Clinton Rt. 54 138 kV line | Reconductor to 1200 A summer emergency capability | IL | IL | Conductor overload following outage to two 345 kV lines. | BRP |  | Reliability | 2019-12-01 | 2019-12-01 | 138 | 138 | Y | 29400000 | Bottom-Up
A in MTEP19 | B>A | Central | AmerenIL | 9840 | Reconfigure Washington Street 138 kV Substation into ring bus | Install 138 kV Ring Bus | IL | IL | Local load serving need and operating flexibility. Existing equipment would be loaded above rating for an outage to the Brokaw-Normal East 138 kV line with Hennepin Generator #2 offline. | Other |  | Load Growth | 2020-06-01 | 2020-06-01 | 138 | 138 | Y | 13300000 | Bottom-Up
A in MTEP19 | B>A | Central | AmerenIL | 9844 | New Normal East-McLean 138 kV Line | Construct 138 kV line | IL | IL | Local area support due to load growth in the Bloomington-Normal area. Will provided an additional transmission supply to the northeast portion of the area. | Other |  | Load Growth | 2020-12-01 | 2020-12-01 | 138 | 138 | Y | 22600000 | Bottom-Up
A in MTEP19 | B>A | Central | AmerenIL | 9851 | Reconductor Edwards-Kewanee 138 kV line (7423) | Reconductor Ameren portion to 1200 A summer emergency capability | IL | IL | Age and condition of facilities | Other |  | Age and Condition | 2019-06-01 | 2019-06-01 | 138 | 138 | Y | 600000 | Bottom-Up
A in MTEP19 | B>A | Central | AmerenIL | 9857 | New Jarvis 345/138 kV Substation | Establish 345/138 kV Substation, connect to 138 kV system in Collinsville-O'Fallon-Highland, Illinois area | IL | IL | Area voltage issues with loss of two 138 kV lines. | BRP |  | Reliability | 2019-12-01 | 2019-12-01 | 345 | 138 | Y | 62300000 | Bottom-Up
A in MTEP19 | B>A | Central | AmerenIL | 11906 | Upgrade Casey West-Kansas 345 kV line | Increase clearance to ground. | IL | IL | Overload for concurrent outages of two EHV lines in AEP. | BRP |  | Reliability | 2022-06-01 | 2022-06-01 | 345 | 0 | Y | 506200 | Bottom-Up
A in MTEP19 | B>A | Central | AmerenIL | 11907 | New Mackinaw (Lilly) 138/34.5 kV substation ring bus | Establish 138 kV ring bus. | IL | IL | Increased reliability | Other |  | Reliability | 2021-12-01 | 2021-12-01 | 138 | 0 | Y | 8800000 | Bottom-Up
A in MTEP19 | B>A | Central | AmerenIL | 11908 | New Towerline (Formerly Powerton Tap) 138 kV breaker 138 kV substation | Establish 138 kV ring bus at the intersection of Havana-Danvers-1352 and Tazewell-San Jose Rail-1367 138 kV Lines. | IL | IL | Increased reliability | Other |  | Reliability | 2019-12-01 | 2019-12-01 | 138 | 0 | Y | 18300000 | Bottom-Up
A in MTEP19 | B>A | Central | AmerenIL | 11923 | New Ridge 138 kV substation ring bus | Establish 138 kV ring bus. | IL | IL | Increased reliability | Other |  | Reliability | 2020-12-01 | 2020-12-01 | 138 | 0 | Y | 15300000 | Bottom-Up
A in MTEP19 | B>A | Central | AmerenIL | 11928 | Convert Commodore 230 kV substation to 345 kV substation | Install spare 345/230/138 kV transformer. Install second 345/230 kV, 375 MVA transformer. Rebuild Commodore-North Coulterville 230 kV line for 345 kV use. | IL | IL | Increased reliability | Other |  | Reliability | 2022-12-01 | 2022-12-01 | 345 | 230 | Y | 42800000 | Bottom-Up
A in MTEP19 | B>A | Central | AmerenIL | 11929 | Aster Substation - Convert North Coulterville 230 kV substation to 345 kV substation | Install 345/138 kV, 560 MVA transformer, 345 kV and 138 kV ring bus on a new Aster Substation site near North Coulterville Substation. Rebuild North Coulterville-Tilden (Prest) 138 kV Line to double circuit with 2000A emergency capability. Rebuild 7 miles of the existing Cahokia – Pinckneyville – 1 230 kV line to 345 kV 3000 A capability between the Prairie State 345 kV switchyard and the existing North Coulterville 230/138 kV substation. 345 kV line. Route the rebuilt line into the Prairie State switchyard. | IL | IL | Increased reliability | Other |  | Reliability | 2021-12-01 | 2021-12-01 | 345 | 138 | Y | 25000000 | Bottom-Up
A in MTEP19 | B>A | Central | AmerenIL | 11933 | Expand Prairie State 345 kV substation for BAAH configuration | Expand the Prairie State switchyard as a breaker-and-a-half configuration, and relocate Prairie State-Mt. Vernon West-4541 and Prairie State-Stallings-4531 345 kV lines to separate bays. Construct new Prairie State-Gateway 345 kV line. | IL | IL | Increased reliability | Other |  | Reliability | 2021-12-01 | 2021-12-01 | 345 | 0 | Y | 60200000 | Bottom-Up
A in MTEP19 | B>A | Central | AmerenIL | 11935 | New North LaSalle 138 kV ring bus | Establish 138 kV ring bus | IL | IL | Increased reliability | Other |  | Reliability | 2019-06-01 | 2019-06-01 | 138 | 0 | Y | 9200000 | Bottom-Up
A in MTEP19 | B>A | Central | AmerenIL | 11944 | Rebuild Mt. Vernon West 138 kV bus | Rebuild 138 kV bus as a breaker-and-a-half arrangement. | IL | IL | Increased reliability | Other |  | Reliability | 2019-12-01 | 2019-12-01 | 138 | 0 | Y | 19200000 | Bottom-Up
A in MTEP19 | B>A | Central | AmerenIL | 11947 | New Greenback (formerly Monsanto) 138 kV substation ring bus | Construct 6-position 138 kV ring bus. | IL | IL | Increased reliability | Other |  | Reliability | 2022-06-01 | 2022-06-01 | 138 | 0 | Y | 17500000 | Bottom-Up
A in MTEP19 | B>A | Central | AmerenIL | 11948 | New Miles 345/138 kV substation | Establish 345/138 kV Substation near the tap point to Alton Steel in the Wood River-Stallings-1456 and Wood River-North Staunton-1456 Lines. | IL | IL | Increased reliability | Other |  | Reliability | 2021-12-01 | 2021-12-01 | 345 | 138 | Y | 44800000 | Bottom-Up
A in MTEP19 | B>A | Central | AmerenIL | 11950 | New Greenville McCord 138 kV ring bus | Establish 138 kV ring bus | IL | IL | Increased reliability | Other |  | Reliability | 2018-12-01 | 2018-12-01 | 138 | 0 | Y | 12400000 | Bottom-Up
A in MTEP19 | B>A | Central | AmerenIL | 11951 | New Crossville West 138 kV ring bus | Establish 138 kV ring bus. Interconnect solar farm J800 | IL | IL | Increased reliability and provide interconnection facilities for the J800 solar farm. | Other |  | Reliability | 2021-12-01 | 2021-12-01 | 138 | 0 | Y | 10800000 | Bottom-Up
A in MTEP19 | B>A | Central | AmerenIL | 11952 | New Barrel (formerly Aviston Tap) 138 kV substation | Establish 138 kV ring bus | IL | IL | Increased reliability | Other |  | Reliability | 2021-12-01 | 2021-12-01 | 138 | 0 | Y | 12400000 | Bottom-Up
A in MTEP19 | B>A | Central | AmerenIL | 11953 | New Bureau (Formerly Princeton Tap) 138 kV substation | Establish 138 kV ring bus | IL | IL | Increased reliability | Other |  | Reliability | 2019-12-01 | 2019-12-01 | 138 | 0 | Y | 7900000 | Bottom-Up
A in MTEP19 | B>A | Central | AmerenIL | 11955 | New Otego (formerly Bluff City) 138 kV substation ring bus | Establish 138 kV ring bus | IL | IL | Increased reliability | Other |  | Reliability | 2021-12-01 | 2021-12-01 | 138 | 0 | Y | 17300000 | Bottom-Up
A in MTEP19 | B>A | Central | AmerenIL | 11956 | New Jasper 138 kV substation ring bus | Establish 138 kV ring bus | IL | IL | Increased reliability | Other |  | Reliability | 2021-12-01 | 2021-12-01 | 138 | 0 | Y | 13100000 | Bottom-Up
A in MTEP19 | B>A | Central | AmerenIL | 11966 | New Gateway 345/138 kV substation | New 345-138 kV Substation, 5-345 kV breakers, new 345/138 kV transformer, 138 kV, 3000 A transformer PCB, two new 138 kV buses with 4 138 kV positions each. Install 345 kV ring bus. Reconfigure exisitng 138 kV Venice buses. Connect to Cahokia-Roxford-4 345 kV Line. | IL | IL | Increased reliability | Other |  | Reliability | 2021-12-01 | 2021-12-01 | 345 | 138 | Y | 114500000 | Bottom-Up
A in MTEP19 | B>A | Central | AmerenIL | 11971 | Reconfigure Jenkins (Formerly Grand Tower) 138 kV substation to BAAH | Establish a Breaker-and-a Half 138 kV bus arrangement | IL | IL | Increased reliability | Other |  | Reliability | 2023-12-01 | 2023-12-01 | 138 | 0 | Y | 22100000 | Bottom-Up
A in MTEP19 | B>A | Central | AmerenIL | 11972 | Reconfigure Redhawk (formerly Midway) 138/34.5 kV substation to BAAH | Establish a Breaker-and-a Half 138 kV bus arrangement | IL | IL | Increased reliability | Other |  | Reliability | 2022-12-01 | 2022-12-01 | 138 | 0 | Y | 20600000 | Bottom-Up
A in MTEP19 | B>A | Central | AmerenIL | 12846 | Reconfigure Kickapoo 138 kV substation to BAAH | Rebuild Kickapoo Substation 138 kV bus as a Breaker-and-a-Half. | IL | IL | Age and condition of existing facilities. | Other |  | Age and Condition | 2021-12-01 | 2021-12-01 | 138 | 0 | Y | 12400000 | Bottom-Up
A in MTEP19 | B>A | Central | AmerenIL | 12964 | New Boar 138 kV breaker substation | Install 138 kV breaker station at the Kewanee South Street tap. Needed: 3-2000 A PCB's. | IL | IL | Increased reliability | Other |  | Reliability | 2021-09-01 | 2021-09-01 | 138 | 0 | Y | 8500000 | Bottom-Up
A in MTEP19 | B>A | Central | AmerenIL | 13545 | New Oakley (Formerly Otto) 138 kV breaker substation | Construct a 3-position initial/4-position ultimate 138 kV ring bus at the Schram City Tap in the Pana-Midway-1466 138 kV Line. Utilize 2000 A equipment. | IL | IL | Increased reliability and operating flexibility in the area. | Other |  | Reliability | 2021-12-01 | 2021-12-01 | 138 | 0 | Y | 10900000 | Bottom-Up
A in MTEP19 | B>A | Central | AmerenIL | 13693 | New Arland (Matooon) 345/138 kV substation | Install new substation at intersection of Mattoon West-Chesterville 138 kV line and the Faraday-Kansas 345 kV line. (name to be determined) | IL | IL | Transient Voltage Recovery issues with the outage of Neoga-Mattoon West and Kansas-Mattoon East 138 kV lines. | BRP |  | Reliability | 2022-12-01 | 2022-12-01 | 345 | 138 | Y | 21200000 | Bottom-Up
A in MTEP19 | B>A | Central | AmerenIL | 13704 | New FACTS Device at Fargo 138 kV substation | Install 138 kV +250/-100 Mvar FACTS device. Install new breaker H5 on 138 kV BAAH to provide connection. | IL | IL | Dynamic reactive support in the Peoria Area. | Other |  | Reliability | 2019-12-01 | 2019-12-01 | 138 | 0 | Y | 30300000 | Bottom-Up
A in MTEP19 | B>A | Central | AmerenIL | 13706 | Reconfigure Mt. Vernon 42nd Street 138 kV substation to ring bus | Install initial 4-position (ultimate 6-position) 138 kV ring bus. | IL | IL | Increase reliability and operating flexibility in the area | Other |  | Reliability | 2021-12-01 | 2021-12-01 | 138 | 0 | Y | 8400000 | Bottom-Up
A in MTEP19 | B>A | Central | AmerenIL | 13707 | New Merlot 345 kV substation ring bus | Install 3000A 138 kV Ring bus at the Campbell Hill Junction. Add breaker at Steelville on 1636 line. | IL | IL | Increase reliability and operating flexibility in the area. | Other |  | Reliability | 2021-06-01 | 2021-06-01 | 138 | 0 | Y | 10300000 | Bottom-Up
A in MTEP19 | B>A | Central | AmerenIL | 13795 | Rebuild Cahokia-Roxford to 345 double circuit | Rebuild from Gateway to Roxford as double ckt 345kV. Install 345kV, 3000A SE capable conductor on each side of the tower. Replace structure 161 at Gateway Substation. OPGW required between Gateway to Roxford. | IL | IL | A field review of the structures from the new Gateway 345/138 kV Substation site (near Tower 160) to Roxford Substation revealed the need to replace the Cor-Ten steel towers. | Other |  | Age and Condition | 2020-12-01 | 2020-12-01 | 345 | 0 | Y | 32700000 | Bottom-Up
A in MTEP19 | B>A | Central | AmerenIL | 14224 | Rebuild Woodhall-Spring Bay 138 kV line 1648 | Rebuild 636 ACSR Rook to 477 ACSR T2 capability. | IL | IL | Structures to be replaced due to age and condition. | Other |  | Age and Condition | 2018-12-15 | 2018-12-15 | 138 | 0 | Y | 7200000 | Bottom-Up
A in MTEP19 | B>A | Central | AmerenIL | 14885 | Reconfigure Mahomet 138 kV substation | Install initial 5-position (ultimate 6-position) ring bus at Mahomet Substation. Double circuit the Mahomet tap section of the RIS-NCMP-1592 line (1.55 miles) to create an in/out supply. | IL | IL | Increase system reliability. | Other |  | Reliability | 2021-12-01 | 2021-12-01 | 138 | 0 | Y | 12000000 | Bottom-Up
A in MTEP19 | B>A | Central | AmerenIL | 15204 | Rebuild Muddy-West Frankfort East 138 kV line to 2000A | Rebuild the MUDY-WFRE-1 circuit using conductor capable of 2000A under summer emergency conditions. Replace breaker 1599, switches 1594, 1579L, 1599L, 1599B and 1589L and 556 kcmil ACSR bus conductor on the MUDY-WFRE-1 position at Muddy Substation with equipment capable of a minimum of 2000A under summer emergency conditions. Replace breaker 1522 and switches 1522B and 1522L at West Frankfort East Substation with equipment capable of a minimum of 2000A under summer emergency conditions. Install OPGW. | IL | IL | A field condition review of the line revealed the need for structure replacements. Conductor capable of carrying 2000A under summer emergency conditions was chosen to provide sufficient 138 kV outlet from the 345 kV hub at West Frankfort East under contingency conditions. | Other |  | Age and Condition | 2019-06-01 | 2019-06-01 | 138 | 0 | Y | 19100000 | Bottom-Up
A in MTEP19 | B>A | Central | AmerenIL | 15206 | Rebuild Gilman South-Watseka 138 kV line 1388 to 1800A | Rebuild the GILS-WATK-1388 line from Gilman South Substation to Watseka Substation using conductor capable of 1800A under summer emergency conditions. Relay upgrades required at Gilman South and Watseka Substations. Install OPGW. | IL | IL | A field condition review of the line revealed the need to replace approximately 30% the structures and conductors. In addition, NERC violations to 3rd party low-voltage underbuild were detected on over 60% of the line. The decision to rebuild with conductors capable of carrying 1800A under summer emergency conditions was made to reduce existing MISO flowgate congestion concerns in the area. | Other |  | Age and Condition | 2019-12-01 | 2019-12-01 | 138 | 0 | Y | 12000000 | Bottom-Up
A in MTEP19 | B>A | Central | AmerenIL | 15207 | Rebuild Albion South-Olney North 138 kV line | Rebuild 28 miles of the Albion South to Olney North 138 kV line. Replace existing 556 ACSR conductor with conductor having a minimum capability of 2000A under summer emergency conditions. The rebuild will consist of replacing 229 structures. Install OPGW. | IL | IL | A field condition review of the line revealed the need for structure replacements. Due to the age and condition of the remaining structures and the requirement to add OPGW, the decision was made to perform a total rebuild. | Other |  | Age and Condition | 2018-05-17 | 2018-05-17 | 138 | 0 | Y | 11000000 | Bottom-Up
A in MTEP19 | B>A | Central | AmerenIL | 15224 | New Hornsby 138 kV substation for Cardinal Point Wind Farm | Install initial 3-position ring bus on the Macomb Niota-1 138 kV line. | IL | IL | Interconnection for the J456 (Cardinal Point) wind farm project. | GIP |  |  | 2019-12-01 | 2019-12-01 | 138 | 0 | Y | 7283395 | Externally Driven
A in MTEP19 | B>A | Central | AmerenIL | 15267 | Reconfigure Herrin East 138 kV substation to ring bus | Install initial 4-position ring bus at the existing Herrin East substation location | IL | IL | Increased reliability on the area distribution system and increased operating flexibility on the transmission system. | Other |  | Reliability | 2022-12-01 | 2022-12-01 | 138 | 0 | Y | 7500000 | Bottom-Up
A in MTEP19 | B>A | Central | AmerenIL | 15269 | Rebuild North 27th St. Decatur-ADM North 138 kV line (1604) | Rebuild the North 27th Street Decatur-ADM North-1604 138 kV line with conductor capable of 2000A under summer emergency conditions. Replace 2500 Kcmil AAC bus at ADM North with bus capable of 2000A | IL | IL | Age and condition of the existing structures and conductor necessitated the need to rebuild the line. | Other |  | Age and Condition | 2019-12-01 | 2019-12-01 | 138 | 0 | Y | 755957 | Bottom-Up
A in MTEP19 | B>A | Central | AmerenIL | 15324 | New Howlett 138 kV substation for J756 interconnection | Install new ring bus breaker station on the Fogarty-Mason City West line. | IL | IL | Interconnection for the J756 Sugar Creek wind farm connection. | GIP |  |  | 2020-06-01 | 2020-06-01 | 138 | 0 | Y | 6900000 | Externally Driven
A in MTEP19 | B>A | Central | AmerenIL | 15325 | New 345 kV ring bus for J757 Interconnection | Install new 345 kV ring bus on the Austin-Meredosia-4527 line | IL | IL | Interconnection for the J757 Lincoln Land wind farm connection. | GIP |  |  | 2020-10-31 | 2020-10-31 | 345 | 0 | Y | 1000000 | Externally Driven
A in MTEP19 | B>A | Central | AmerenIL | 15330 | Rebuild Gifford-Rantoul 138 kV line (1500) | Rebuild Gifford-Rantoul-1500 138 kV line to 1200A with T-2 conductor | IL | IL | A field review of the line revealed the need for structure replacements on the majority of the line due to age and condition. T-2 conductor was used due to galloping concerns in the area. | Other |  | Age and Condition | 2018-05-25 | 2018-05-25 | 138 | 0 | Y | 3200000 | Bottom-Up
A in MTEP19 | B>A | Central | AmerenIL | 15488 | Sheldon South - Morrison Ditch 138 kV line: Rebuild | Rebuild line from Sheldon South to Morrison Ditch | IL | IL | Structures required to be replaced due to age and condition as well as clearance issues. | Other |  | Age and Condition | 2020-12-31 | 2020-12-31 | 138 | 0 | Y | 3000000 | Bottom-Up
A in MTEP19 | B>A | Central | AmerenIL | 15489 | Reconfigure Meppen North Ring 138 kV substation | At the Meppen North 138 kV substation, construct a 4-position (6-ultimate) ring bus having a minimum continuous capability of 2000A | IL | IL | The project is needed to facilitate the proposed addition of a 138/69 kV transformer by PPI. The construction of this ring bus would provide a reliable source for the planned interconnection, and improve operating flexibility of the existing system. | Other |  | Reliability | 2022-06-01 | 2022-06-01 | 138 | 0 | Y | 8944019 | Bottom-Up
A in MTEP19 | B>A | Central | AmerenIL | 15490 | New Radnor Ring 138 kV bus addition | Install 4 position 138 kV ring bus | IL | IL | Request from distribution to increase reliability and operating flexibility in the area. | Other |  | Reliability | 2022-06-01 | 2022-06-01 | 138 | 0 | Y | 9000000 | Bottom-Up
A in MTEP19 | B>A | Central | AmerenIL | 15491 | Upgrade North Decatur-East Main Street 138 kV line (1522) | Increase rating to 100C. Rebuild the segment from str. 39 to Decatur North 27th St. with 954 Cardinal ACSS. OPGW required. Jumper replacements at Decatur North 27th St. | IL | IL | Structure replacements required to to age and condition as well as conductor clearance issues. | Other |  | Age and Condition | 2020-06-01 | 2020-06-01 | 138 | 0 | Y | 2100000 | Bottom-Up
A in MTEP19 | B>A | Central | AmerenIL | 15492 | Upgrade North Decatur-North 27th Street 138 kV line (1602) | Structure replacements required. Replace 1272 Jumpers on either side of wavetrap at N. Decatur. | IL | IL | Structure replacements required due to clearance issues. Jumpers replaces to increase line capacity for future growth. | Other |  | Reliability | 2020-12-01 | 2020-12-01 | 138 | 0 | Y | 500000 | Bottom-Up
A in MTEP19 | B>A | Central | AmerenIL | 15494 | Rebuild Rising-N Champaign-Leverett Road 138 kV line (1592) | Rebuild Champaign-Leverett Road section to 954 T-2 conductor. | IL | IL | A field evaluation revealed the need for structure replacements due to age and condition. | Other |  | Age and Condition | 2020-12-01 | 2020-12-01 | 138 | 0 | Y | 5791779 | Bottom-Up
A in MTEP19 | B>A | Central | AmerenIL | 15497 | Rebuild Marblehead N–Quincy 3rd & Jefferson East 138 kV line | Rebuild line with 477 T-2 Hen. Upgrade terminal equipment to 2000A and perform relay upgrades at Marblehead N substation | IL | IL | Increased clearance is required to achieve the rating necessary for projected operating conditions. Structure replacements for over 50% of the line is required due to age and condition. Therefore, the decision was made to rebuild the line. | Other |  | Reliability | 2020-12-01 | 2020-12-01 | 138 | 0 | Y | 5500000 | Bottom-Up
A in MTEP19 | B>A | Central | AmerenIL | 15498 | Rebuild Crab Orchard-Muddy 138 kV line | Rebuild line to 2000A capability. | IL | IL | Rebuild necessary due to aging infrastructure and clearance issues | Other |  | Age and Condition | 2019-12-01 | 2019-12-01 | 138 | 0 | Y | 14000000 | Bottom-Up
A in MTEP19 | B>A | Central | AmerenIL | 15499 | Rebuild Jerseyville NW-Austin 138 kV line | Rebuild line 10 1600A | IL | IL | Aging infrastructure and clearance issues require the line to be rebuilt. | Other |  | Age and Condition | 2020-12-01 | 2020-12-01 | 138 | 0 | Y | 34300000 | Bottom-Up
A in MTEP19 | B>A | Central | AmerenIL | 15502 | Rebuild Mt. Vernon West-Mt. Vernon 42nd St. 138 kV line | Rebuild MTVS-MTVW-1336 between Mt. Vernon West and Mt. Vernon 42nd St. Provide a double circuit between Mt. Vernon West and Mt. Vernon World Color Press to eliminate the current World Color Tap on the MTVS-MTVW-1336 line. | IL | IL | A field condition review of the line revealed the need for structure replacements due to insufficient ground and obstacle clearances on the 138 kV MTVS-MTVW-1336 line for the sections from Mt. Vernon West to Mt. Vernon World Color Tap, and Mt. Vernon World Color Tap to Mt. Vernon 42nd St. | Other |  | Age and Condition | 2019-06-01 | 2019-06-01 | 138 | 0 | Y | 7300000 | Bottom-Up
A in MTEP19 | B>A | Central | AmerenIL | 15525 | Rebuild RS Wallace-Spring Bay 138 kV line | Rebuild 10 miles of the RSWA-SPBA-1344 line, from Str 12 to Spring Bay with conductor capable of 1300 Amp minimum under summer emergency conditions. A 3.7 mile section of CAT2-Hines-1357 will also be reconductored with the same conductor because it occupies the other position on the double circuit. Reconductor 1.6 miles of the RSWA-SPBA-1344 line from RS Wallace to Str 12 and 1.5 miles on the CAT2-Hines-1357 line Str 2 to Str 12 with ACCR 557-T16 26/7 DOVE. | IL | IL | A field condition review of the line revealed the need for structure replacements. | Other |  | Age and Condition | 2019-12-01 | 2019-12-01 | 138 | 0 | Y | 15300000 | Bottom-Up
A in MTEP19 | B>A | Central | AmerenIL | 15527 | New Heath 138 kV Substation (Robinson Marathon North) | Install new 6 position ring bus with 3 transformer positions and 3 line positions. Install new 0.8 mile 138 kV line from the Robinson Marathon substation to the new ring bus. Reconductor the existing 138 kV tap off the HUTY-ROBM line. | IL | IL | Customer requested for increased reliability. | Other |  | Age and Condition | 2020-12-01 | 2020-12-01 | 138 | 0 | Y | 12717801 | Bottom-Up
A in MTEP19 | B>A | Central | AmerenIL | 15528 | New Dirksen (East Springfield) 138 kV substation | Construct 6-position Ring Bus | IL | IL | Improve reliability and operating flexibility of Ameren transmission system. | Other |  | Reliability | 2021-12-01 | 2021-12-01 | 138 | 0 | Y | 17300000 | Bottom-Up
A in MTEP19 | B>A | Central | AmerenIL | 16224 | New Alta Wind Farms (J474) interconnection | Connect 144 MW wind farm at Tabor Substation | IL | IL | Provide generator interconnection for Alta Farms 2 | GIP |  |  | 2020-03-01 | 2020-03-01 | 138 | 0 | Y | 0 | Externally Driven
A in MTEP19 | B>A | Central | AmerenIL | 16225 | New Yates 138 kV Substation for Morgan-Scott Counties Solar Interconnection | Install new ring bus substation on the Jacksonville Industrial Park-Meredosia East-1612 138 kV line to provide the interconnection for Morgan-Scott Counties Solar (J641) solar farm connection. | IL | IL | New solar farm interconnection | GIP |  |  | 2021-06-01 | 2021-06-01 | 138 | 0 | Y | 6722298 | Externally Driven
A in MTEP19 | B>A | Central | AmerenIL | 16226 | New Green-Scott Counties Solar (J644) interconnection | Connect 110 MW solar connection at Jerseyville NW Substation | IL | IL | New solar farm connection | GIP |  |  | 2020-12-01 | 2020-12-01 | 138 | 0 | Y | 500000 | Externally Driven
A in MTEP19 | B>A | Central | AmerenIL | 16547 | Relocate Mapleridge-Tazewell 345 kV line (4528) | Relocation of approximately 0.4 miles of Ameren's existing Mapleridge-Tazewell-4528 345 kV line at the Edwards Power Plant. | IL | IL | Eliminate limiting section of failed 345 kV cable located at Edwards Substation. | Other |  | Age and Condition | 2020-06-01 | 2020-06-01 | 345 | 0 | Y | 4300000 | Bottom-Up
A in MTEP19 | B>A | Central | AmerenIL | 16550 | New Prairie State Solar (J808) interconnection | Provide interconnection facilities for a 99 MW solar farm at North Coulterville. Construct new position as part of a 5-position 138 kV ring bus at Aster Substation (North Coulterville). | IL | IL | Interconnection facilities for a solar farm | GIP |  |  | 2020-06-01 | 2020-06-01 | 138 | 0 | Y | 19300000 | Externally Driven
A in MTEP19 | B>A | Central | AmerenIL | 16551 | New Cincinnati 138 kV substation | Install new 138 kV ring bus with an in/out supply from the Towerline-Powerton 138 kV line at the existing Cincinnati distribution substation location. | IL | IL | Distribution driven for 69 kV capacity | Other |  | Load Growth | 2021-12-01 | 2021-12-01 | 138 | 0 | Y | 7668917 | Bottom-Up
A in MTEP19 | B>A | Central | AmerenIL | 16553 | Rebuild Cat 2-Hines 138 kV line | Rebuild a 3.7 mile section of CAT2-Hines-1357 to 1200A minimum | IL | IL | Age and condition of existing structures and conductor requires a rebuild of the line. | Other |  | Age and Condition | 2019-12-01 | 2019-12-01 | 138 | 0 | Y | 6932273 | Bottom-Up
A in MTEP19 | B>A | Central | AmerenIL | 16584 | Rebuild Cat 2 138 kV substation | Upgrade existing 138 kV ring bus, replacing breakers, switches and wave traps with new equipment having a minimum 2000 amp capability. | IL | IL | Ameren is purchasing the substation and will upgrade the equipment due to age and condition. | Other |  | Age and Condition | 2020-12-02 | 2020-12-02 | 138 | 0 | Y | 5117992 | Bottom-Up
A in MTEP19 | B>A | Central | AmerenIL | 16784 | Rebuild Pana-Midway 138 kV line (1466) | Rebuild 27.68 miles the Pana-Midway-1466 138 kV line from Pana to structure 237 (Schram Tap) using T-2 conductor with a capable of carrying 2000 amps under summer emergency conditions. | IL | IL | Age and condition of existing structures necessitated the rebuild of the line | Other |  | Age and Condition | 2020-12-01 | 2020-12-01 | 138 | 0 | Y | 21241117 | Bottom-Up
A in MTEP19 | B>A | Central | AmerenIL | 16787 | Rebuild SJRL-INTR 138 kV line (1318) | Rebuild line from New Holland to Kickapoo. Replace 2 switches at Mason Substation. Replace 2 structures between Mason and New Holland. Replace 5 structures between New Holland and Interstate. | IL | IL | Age and condition of existing structures necessitated the rebuild of the line. | Other |  | Age and Condition | 2020-12-01 | 2020-12-01 | 138 | 0 | Y | 11109911 | Bottom-Up
A in MTEP19 | B>A | Central | AmerenIL | 16788 | Rebuild MTVW-SCNT 138 kV line (1546) | Rebuild line to 110 degrees C. | IL | IL | Age and condition of existing facilities required the need for structure replacements. | Other |  | Age and Condition | 2020-12-01 | 2020-12-01 | 138 | 0 | Y | 2311664 | Bottom-Up
A in MTEP19 | B>A | Central | AmerenIL | 16789 | Rebuild Ashley-West Frankfort 138 kV line (1536) | Rebuild line from Ashley to West Frankfort | IL | IL | Age and condition of existing structures requires the rebuild of the line. | Other |  | Age and Condition | 2020-12-01 | 2020-12-01 | 138 | 0 | Y | 26034438 | Bottom-Up
A in MTEP19 | B>A | Central | AmerenIL | 16790 | Rebuild Grand Tower-Steelville 138 kV line (1636) | Rebuild line from Grand Tower to Steelville | IL | IL | Age and condition of existing structures requires the rebuild of the line. | Other |  | Age and Condition | 2020-12-01 | 2020-12-01 | 138 | 0 | Y | 9100000 | Bottom-Up
A in MTEP19 | B>A | Central | AmerenIL | 16791 | Rebuild OREA -ADMIN 138 kV line (1606) | Rebuild line from Oreana to ADM North | IL | IL | Age and condition of existing structures requires the need to rebuild the line. | Other |  | Age and Condition | 2020-12-01 | 2020-12-01 | 138 | 0 | Y | 654435 | Bottom-Up
A in MTEP19 | B>A | Central | AmerenIL | 16792 | Rebuild Sidney-SW Campus 138 kV line (1312) | Rebuild line from Sidney to Southwest Campus | IL | IL | Age and condition requires the rebuild of the line. | Other |  | Age and Condition | 2020-12-01 | 2020-12-01 | 138 | 0 | Y | 7179354 | Bottom-Up
A in MTEP19 | B>A | Central | AmerenIL | 16794 | Replace Cahokia-Meramec 1&2 138 kV Structures | Replace structures on the Cahokia-Meramec 1 & 2 line | IL | IL | Age and condition requires the need for structure replacements. | Other |  | Age and Condition | 2020-12-01 | 2020-12-01 | 138 | 0 | Y | 2504181 | Bottom-Up
A in MTEP19 | B>A | Central | AmerenIL | 16796 | Rebuild Oreana-ADM North 138 kV line (1610) | Rebuild line from Oreana to ADM North | IL | IL | Age and condition of existing structures necessitated the rebuild of the line. | Other |  | Age and Condition | 2020-12-01 | 2020-12-01 | 138 | 0 | Y | 420351 | Bottom-Up
A in MTEP19 | B>A | West | MEC | 15678 | Sub 17: New 161 kV Capacitors | Install two new 161 kV 25 MVAr capacitor banks at Sub 17. | IL | IL | Needed to mitigate low voltages following Category P6 (N-1-1) contingencies. | BRP |  |  | 2020-06-01 | 2020-06-01 | 161 | 0 | Y | 1500000 | Bottom-Up
A in MTEP19 | B>A | Central | PPI | 15769 | New Disco 138/69/12.47 kV Substation | 1) New (Ameren) Grove-(PPI) Disco 138 kV substation 2) New Disco 138/69 kV and 69/12.47 kV substation | IL | IL | Distribution Reliability Provides independent source for Western Illinois Power Cooperative (WIEC). Allows WIEC to backup Lomax, Carthage and Powellton substations. | Other |  | Reliability | 2023-12-31 | 2023-12-31 | 138 | 12.47 | Y | 4000000 | Bottom-Up
A in MTEP19 | B>A | Central | PPI | 15774 | New Pleasant View 138/69 kV Substation | 1) New (Ameren) Dempsey-(PPI) Pleasant View 138 kV line 2) New Pleasant View 138/69-34.5 kV Substation | IL | IL | Distribution Reliability Provide an alternate source to feed Shelby Electric Cooperative's Blue Mound, Taylorville and Grove City substations. Existing 34.5 kV system is inadequate to accommodate new load or backup existing substations. | Other |  | Reliability | 2023-12-31 | 2023-12-31 | 138 | 69 | Y | 4700000 | Bottom-Up
A in MTEP19 | B>A | Central | PPI | 15786 | Rebuild Naples 69 kV River Crossing | Rebuild Naples 69 kV Illinois River crossing which will include OPGW. | IL | IL | Age and condition Original line was built in 1953. | Other |  | Age and Condition | 2020-12-31 | 2020-12-31 | 69 | 69 | Y | 900000 | Bottom-Up
A in MTEP19 | B>A | Central | PPI | 15814 | Rebuild Kampsville 69 kV River Crossing | Rebuild Kampsville 69kV Illinois River crossing which will include OPGW. | IL | IL | Age and condition Original line was built in 1954 and modified in 1996. | Other |  | Age and Condition | 2020-12-31 | 2020-12-31 | 69 | 69 | Y | 900000 | Bottom-Up
A in MTEP19 | B>A | Central | PPI | 15815 | New Fancy Creek-Middletown 69 kV Line | New Athens-Middletown 69 kV line | IL | IL | Distribution Reliability Provide alternative feed to Middletown substation | Other |  | Reliability | 2022-12-31 | 2022-12-31 | 69 | 69 | Y | 7550000 | Bottom-Up
A in MTEP19 | B>A | Central | PPI | 15817 | New Grand Island-Oakford 69 kV Line | New Grand Island-Oakford 69 kV line | IL | IL | Distribution Reliability Provide alternative feed to Oakford substation | Other |  | Reliability | 2022-12-31 | 2022-12-31 | 69 | 69 | Y | 6350000 | Bottom-Up
A in MTEP19 | B>A | Central | PPI | 15825 | New Mechanicsburg-Taylorville 69 kV Line | New Mechanicsburg-Taylorville 69 kV line | IL | IL | Distribution Reliability Provide alternative feed to Mechanicsburg and Taylorville substations | Other |  | Reliability | 2023-12-31 | 2023-12-31 | 69 | 69 | Y | 7050000 | Bottom-Up
A in MTEP19 | B>A | Central | PPI | 15827 | Rebuild Nortonville Tap-Murrayville Jct 69 kV Line | Rebuild and Reconductor Murrayville Jct-Nortonville Tap 69 kV line. Change Line from 3/0 ACSR to 336.4 MCM ACSR with OPGW. | IL | IL | Age and condition | Other |  | Age and Condition | 2020-12-31 | 2020-12-31 | 69 | 69 | Y | 1340000 | Bottom-Up
A in MTEP19 | B>A | Central | PPI | 15828 | Rebuild Nortonville Tap-Jacksonville 69 kV Line | Rebuild and Reconductor Nortonville Tap-Jacksonville 69 kV line. Replace 4/0 conductor with 336.4 MCM ACSR with OPGW. | IL | IL | Age and condition | Other |  | Age and Condition | 2020-12-31 | 2020-12-31 | 69 | 69 | Y | 2984000 | Bottom-Up
A in MTEP19 | B>A | Central | PPI | 15830 | New Shelbyville S.-ISHI 138 kV line | 1) New 7.0 mile line from (Ameren) Shelbyville S.-(PPI) ISHI 34.5 kV line (6.3 miles built to 138 kV specs, .7 miles built to 69 kV specs) 2) New ISHI 138/69-34.5 kV Switching Station, includes an 84 MVA LTC Transformer | IL | IL | Load Growth New 4 MW load addition at ISHI substation | Other |  | Load Growth | 2019-12-31 | 2020-12-31 | 138 | 69 | Y | 7000000 | Bottom-Up
B in MTEP20 | B | Central | AmerenIL | 16144 | Replace Newton 345/138 kV transformer | Replace the existing Newton 345-138 kV unit #1 with a new 700 MVA unit | IL | IL | Local planning criteria violation. Unit above rating with the loss of the CSYW-NWTY-1 and MTVW-XENA-4591 345 kV lines |  |  |  | 2023-06-01 | 2023-06-01 | 345 | 138 | Y |  | Bottom-Up
B in MTEP20 | B | Central | AmerenIL | 18014 | MCLN-OGLE-1382 Reconductor | Reconductor MCLN-OGLE-1382 from McLean to the El Paso tap with a minimum of 1600A conductor. | IL | IL | Needs to be evaluated in future studies |  |  |  | 2027-06-01 | 2027-06-01 | 138 | 0 | Y |  | Bottom-Up
B in MTEP20 | B | Central | AmerenIL | 18270 | Sandburg to LaSalle (ComEd) 345 kV line | Construct a new 345 kV line from Sandburg to the ComEd LaSalle station or the LaSalle – Plano 345 kV line. Install a 345/138 kV step down at Corbin Substation. | IL | IL | This line is to provide support to the LaSalle and Bureau counties. This will allow for future load growth. The transmission system will be at its limit in this area by 2027. |  |  |  | 2027-06-01 | 2027-06-01 | 345 | 138 | Y |  | Bottom-Up
B in MTEP20 | B | Central | AmerenIL | 18336 | Kinmundy-Ramsey E-1 | Increase the line rating of the Avena Tap to Ramsey East 138kV line to 1600A | IL | IL | Mitigation for DPP-2017-August-Central |  |  |  | 2021-06-01 | 2021-06-01 | 138 | 0 | Y |  | Bottom-Up
B in MTEP19 | B | Central | AmerenIL | 15264 | New Lebanon Rt 50 138 kV Substation | Install new 138 kV bulk substation at the Lebanon Rt 50 substation site. Install new 138 kV line from Jarvis Substation as a double circuit on the existing 345 kV to supply the new sub. | IL | IL | Distribution system capacity due to load growth in the Belleville area. |  |  |  | 2023-12-01 | 2023-12-01 | 138 | 0 | Y |  | Bottom-Up
A in MTEP20 | B>A | Central | AmerenIL, AmerenMO | 16984 | Sioux-Meppen North-4 River Xing Rebuild | Rebuild existing river crossing (structures 173-179). | IL,MO | IL,MO | A field condition review of the lines revealed the need for structure and line conductor replacement due to age and condition. |  |  |  | 2021-12-01 | 2021-12-01 | 138 | 0 | Y | 45700000 | Bottom-Up
A in MTEP20 | B>A | Central | AEP | 17684 | Upgrade Greentown 765 kV substation | Rehabilitation and reconfiguration of the 765kV Greentown yard. | IN | IN | 765kV assets at high risk of failure, in poor condition or performing poorly as well as being subject to operational concerns. | Other |  | Age and Condition | 2023-02-15 | 2023-02-15 | 765 | 138 | Y | 70000000 | Bottom-Up
A in MTEP20 | B>A | Central | DEI | 2864 | Centeron to Martinsville 69kV - 69163 ckt. Reconductor | Reconductor the 69kV-69163 ckt - 3.47 miles of 366ACSR 80C and 0.23 miles of 477ACSR 80C to 954ACSR 100C | IN | IN | (N-1) - For the contingency outage of the Bloomington 230/69KV transformer bank# 5 the flow in the Centerton to Martinsville 69163 line exceeds the 80 MVA rating (100C) of the 336 ACSR conductor. A switching procedure at Bloomington to close the 6969 tie breaker upon outage of either Bloomington transformer will alleviate the overload on the Centerton to Martinsville through 2019. | BRP | Not Shared |  | 2021-06-01 | 2021-06-01 | 69 | 0 | NT | 7400000 | Bottom-Up
A in MTEP20 | B>A | Central | DEI | 17484 | Rebuild Wabash River-Water St. 138 kV line (13845) | Wabash River to Water St. 13845 Rebuild with 954ACSR | IN | IN | Line overload identified in MTEP19 analysis - Cat. P2, P4 |  |  |  | 2024-06-01 | 2024-06-01 | 138 | 0 | Y | 16300000 | Bottom-Up
A in MTEP20 | B>A | Central | DEI | 17485 | Rebuild Purdue NW Tap-W. Lafayette Airport 138 kV line (13820) | Purdue NW Tap 2 to W. Lafayette Airport 13820 Rebuild with 954ACSR | IN | IN | Line overload identified in MTEP19 analysis - Cat. P2, P4 |  |  |  | 2024-06-01 | 2024-06-01 | 138 | 0 | Y | 3600000 | Bottom-Up
A in MTEP20 | B>A | Central | DEI | 18284 | J754 Gen. Interconnect | J754 Wind Farm - Gen. Interconnect: 34501 ckt. - 300MW Wind farm; 3-breaker ring bus switching station | IN | IN | J754 Gen Queue - IA executed | GIP |  |  | 2021-03-15 | 2021-10-31 | 345 | 0 | Y | 23000000 | Externally Driven
A in MTEP20 | B>A | Central | DEI | 18285 | WVPA McGrawsville to Bunker Hill 69kV alternate source line | WVPA to build McGrawsville to Bunker Hill 69kV alternate source line - 7.1 miles to be operated N.O. | IN | IN | WVPA desire for back up source to distribution loads |  |  |  | 2021-06-01 | 2021-06-01 | 69 | 0 | Y | 5510000 | Bottom-Up
A in MTEP20 | B>A | Central | DEI | 18286 | Brownstown Sw Sta to Pumpkin Center 69kV Rebuild | 6952 Rbld Pt 2 Brownstown Sw Sta to Pumpkin Center; 10.7 mi. - 477acsr ; Replace the 6952-69123 tie switch on pole #813-1535-02 located just outside Pumpkin Center substation | IN | IN | The assets being addressed in this project fall under one or more of the system programs as outlined in TDSIC Plan filed with Indiana Utility Regulatory Commission. |  |  |  | 2021-12-31 | 2021-12-31 | 69 | 0 | Y | 21400000 | Bottom-Up
A in MTEP20 | B>A | Central | DEI | 18287 | Terre Haute S. Vigo to HE Middletown Jct 69kV Rebuild | Rbld 6901 circuit from TH Haute S. Vigo sub, pole 802-1158, to HE Middletown Jct, pole 802-1315, using light-duty steel poles, 477ACSR conductor & OPGW static. Rpl switch #64LB with two 2000A switches | IN | IN | The assets being addressed in this project fall under one or more of the system programs as outlined in TDSIC Plan filed with Indiana Utility Regulatory Commission. |  |  |  | 2021-12-31 | 2021-12-31 | 69 | 0 | Y | 10000000 | Bottom-Up
A in MTEP20 | B>A | Central | DEI | 18288 | Trafalgar Swi Sta to HE Samaria Jct 69kV Rebuild | Rbld transmission line 6949 from Duke Trafalgar Swi Sta & HE Trafalgar sub to HE Samaria Jct using light duty steel poles, 477 ACSR and OPGW. Approximately 4.9 miles. | IN | IN | The assets being addressed in this project fall under one or more of the system programs as outlined in TDSIC Plan filed with Indiana Utility Regulatory Commission. |  |  |  | 2021-12-31 | 2021-12-31 | 69 | 0 | Y | 9800000 | Bottom-Up
A in MTEP20 | B>A | Central | DEI | 18289 | HE Needmore Jct to HE Needmore 69kV Rebuild | 6949 Part 2B - Rebuild transmission line using light duty steel poles, 477 ACSR and OPGW from “HE Needmore Jct” (pole #825-3379) to the HE Needmore substation (pole #825-3418); approximately 2 miles. | IN | IN | The assets being addressed in this project fall under one or more of the system programs as outlined in TDSIC Plan filed with Indiana Utility Regulatory Commission. |  |  |  | 2021-12-31 | 2021-12-31 | 69 | 0 | Y | 4000000 | Bottom-Up
A in MTEP20 | B>A | Central | DEI | 18290 | Purdue University CHP Generation | Purdue University CHP Generation - 15.5MW gas turbines with HRSG unit - non-MISO queue; non-BES | IN | IN | DEI project to serve part of the Purdue campus load with gas fired generation |  |  |  | 2021-07-16 | 2021-07-16 | 138 | 12 | Y | 250000 | Bottom-Up
A in MTEP20 | B>A | Central | DEI | 18304 | Batesville 345kV and 138kV breaker replacements | Batesville 345: Replace (1) 345kV circuit switcher with 345kV SF6 gas circuit breaker ; replace 345kv WT ; Replace (6) 138kV oil circuit breakers with SF6 gas circuit breakers - 13831, 13833, 13839, 13864, 13874, 138345-3 ; replace 13833 and 13874 WTs ; | IN | IN | The assets being addressed in this project fall under one or more of the system programs as outlined in TDSIC Plan filed with Indiana Utility Regulatory Commission. |  |  |  | 2021-12-31 | 2021-12-31 | 345 | 138 | Y | 5300000 | Bottom-Up
A in MTEP20 | B>A | Central | DEI | 18305 | Westwood 345kV / 138kV relays and breakers replacement | Westwood misc station equipment replacement including: upgrade relays on 13806, 13808, 138345-1, Bk2, 138 bus 1 and 2, 138 bus tie ; Replace OCB 13820, 13883 and relays | IN | IN | The assets being addressed in this project fall under one or more of the system programs as outlined in TDSIC Plan filed with Indiana Utility Regulatory Commission. |  |  |  | 2021-12-31 | 2021-12-31 | 345 | 138 | Y | 4900000 | Bottom-Up
A in MTEP20 | B>A | Central | DEI | 18306 | H.E. Batesville 138/12kV new substation | H.E. Batesville 138/12kV substation: new sub to be located in the 13833 ckt between Batesville 345 and Laurel | IN | IN | HE distribution load growth |  |  |  | 2020-12-31 | 2020-12-31 | 138 | 12 | Y | 500000 | Bottom-Up
A in MTEP20 | B>A | Central | DEI | 18307 | Westfield East 69/12kV new substation | Westfield East: new sub - 69/12kv - 22.4 MVA xfmr bank, single phase regulators SCADA/IVVC, 2 breakers, and space for second bank. | IN | IN | Distribution load growth |  |  |  | 2021-06-01 | 2021-06-01 | 69 | 12 | Y | 500000 | Bottom-Up
A in MTEP20 | B>A | Central | DEI | 18308 | Hunts Creek 138/12kV new substation | Hunts Creek 138/12kV substation: new sub to be located in the 13855 ckt between LGE Ghent and DEI Fairview | IN | IN | Distribution load growth |  |  |  | 2021-06-01 | 2021-06-01 | 138 | 12 | Y | 500000 | Bottom-Up
A in MTEP20 | B>A | Central | DEI | 18324 | WVPA Delphi South-6988 Tap Line | New 6.3 mile loop between Delphi South (IPC, Indiana Packers Corp.) and tapping the existing 6988 Line between Flora and Rockfield substations to be built by WVPA | IN | IN | WVPA desire for back up source to distribution loads |  |  |  | 2021-12-31 | 2021-12-31 | 69 | 0 | Y | 5510000 | Bottom-Up
A in MTEP20 | B>A | Central | DEI | 18325 | NSA Crane ULTF 69/12kV new substation | NSA Crane ULTF: new sub - 17 MW new load to be fed from 69193 ckt - located North of existing NSA owned East and West Substations | IN | IN | Distribution load growth |  |  |  | 2021-06-01 | 2021-06-01 | 69 | 12 | Y | 4000000 | Bottom-Up
A in MTEP20 | B>A | Central | DEI | 18326 | Poseyville to HE Winfield 69kV Rebuild | 69139 Rebuild Part 2: Poseyville to HE Winfield TDSIC ; 4.4 miles - N.O. tie line | IN | IN | The assets being addressed in this project fall under one or more of the system programs as outlined in TDSIC Plan filed with Indiana Utility Regulatory Commission. |  |  |  | 2021-12-31 | 2021-12-31 | 69 | 0 | Y | 8800000 | Bottom-Up
A in MTEP20 | B>A | Central | DEI | 18327 | Dresser to S. Vigo 69kV Rebuild | 6901 rebuild from Dresser to S. Vigo with 477ACSR and light-duty steel poles | IN | IN | The assets being addressed in this project fall under one or more of the system programs as outlined in TDSIC Plan filed with Indiana Utility Regulatory Commission. |  |  |  | 2021-12-31 | 2021-12-31 | 69 | 0 | Y | 12000000 | Bottom-Up
A in MTEP20 | B>A | Central | DEI | 18328 | Greencastle N. to Morton Jct. 69kV Rebuild | 6933 rebuild from Greencastle N. to Morton Jct. with 477ACSR and light-duty steel poles | IN | IN | The assets being addressed in this project fall under one or more of the system programs as outlined in TDSIC Plan filed with Indiana Utility Regulatory Commission. |  |  |  | 2021-12-31 | 2021-12-31 | 69 | 0 | Y | 13600000 | Bottom-Up
A in MTEP20 | B>A | Central | DEI | 18329 | Dover to Thorntown 69kV Rebuild | 69134 rebuild from Dover to Thorntown with 477ACSR and light-duty steel poles | IN | IN | The assets being addressed in this project fall under one or more of the system programs as outlined in TDSIC Plan filed with Indiana Utility Regulatory Commission. |  |  |  | 2021-12-31 | 2021-12-31 | 69 | 0 | Y | 9200000 | Bottom-Up
A in MTEP20 | B>A | Central | DEI | 18330 | Westland Jct. to Westland 69kV Rebuild | 69166 rebuild from Westland Jct. to Westland with 477ACSR and light-duty steel poles | IN | IN | The assets being addressed in this project fall under one or more of the system programs as outlined in TDSIC Plan filed with Indiana Utility Regulatory Commission. |  |  |  | 2021-12-31 | 2021-12-31 | 69 | 0 | Y | 13200000 | Bottom-Up
A in MTEP20 | B>A | Central | DEI | 18331 | Whitesville to Advance 69kV Rebuild | 69154 rebuild from Whitesville to Advance with 477ACSR and light-duty steel poles | IN | IN | The assets being addressed in this project fall under one or more of the system programs as outlined in TDSIC Plan filed with Indiana Utility Regulatory Commission. |  |  |  | 2021-12-31 | 2021-12-31 | 69 | 0 | Y | 20600000 | Bottom-Up
A in MTEP20 | B>A | Central | DEI | 18332 | Knightstown to Carthage 69kV Rebuild | 69140 rebuild from Knightstown to Carthage with 477ACSR and light-duty steel poles | IN | IN | The assets being addressed in this project fall under one or more of the system programs as outlined in TDSIC Plan filed with Indiana Utility Regulatory Commission. |  |  |  | 2021-12-31 | 2021-12-31 | 69 | 0 | Y | 9800000 | Bottom-Up
A in MTEP20 | B>A | Central | DEI | 18333 | Greencastle to Greencastle N. 69kV Rebuild | 6933 rebuild from Greencastle to Greencastle N. with 477ACSR and light-duty steel poles | IN | IN | The assets being addressed in this project fall under one or more of the system programs as outlined in TDSIC Plan filed with Indiana Utility Regulatory Commission. |  |  |  | 2021-12-31 | 2021-12-31 | 69 | 0 | Y | 6900000 | Bottom-Up
A in MTEP20 | B>A | Central | DEI | 18334 | Connersville to Glenwood 69kV Rebuild | 6920 rebuild from Connersville to Glenwood with 477ACSR and light-duty steel poles | IN | IN | The assets being addressed in this project fall under one or more of the system programs as outlined in TDSIC Plan filed with Indiana Utility Regulatory Commission. |  |  |  | 2021-12-31 | 2021-12-31 | 69 | 0 | Y | 17300000 | Bottom-Up
A in MTEP20 | B>A | Central | DEI | 18335 | Tate and Lyle Generation | Tate and Lyle (old Staley) Generation - existing sub on the 13808 ckt; 2 units -32.8MW each - non-MISO queue | IN | IN | customer project to serve part of their load with gas fired generation |  |  |  | 2021-04-01 | 2021-04-01 | 138 | 12 | Y | 250000 | Bottom-Up
A in MTEP20 | B>A | Central | IPL | 17564 | Rockville 345 kV Ring Bus | Add one 345 kV breaker to form a ring bus at the Rockville substation. | IN | IN | Adding the 345 kV breaker to form a ring bus allows for the Rockville to Guion and Rockville to Thompson 345 kV lines to remain in service for the Rockville 345-138 kV auto-transformer contingency. This allows for the removal of the operating procedures needed for P6 contingency thermal overloads that are the result of the loss of the Rockville 345-138 kV auto-transformer combined with other elements. |  |  |  | 2020-12-31 | 2020-12-31 | 345 | 0 | Y |  | Bottom-Up
A in MTEP20 | B>A | Central | IPL | 17884 | Southeast #4 Breaker Replacement | Replacement of one (1) 138 kV breaker at Southeast, #4 | IN | IN | Reliability need resulting from the annual short circuit analysis as required by NERC TPL-001-4 R2.3 & R2.8 |  |  |  | 2025-12-31 | 2025-12-31 | 138 | 0 | Y |  | Bottom-Up
A in MTEP20 | B>A | Central | IPL | 17885 | Southeast #6 Breaker Replacement | Replacement of one (1) 138 kV breaker at Southeast, #6 | IN | IN | Reliability need resulting from the annual short circuit analysis as required by NERC TPL-001-4 R2.3 & R2.8 |  |  |  | 2025-12-31 | 2025-12-31 | 138 | 0 | Y |  | Bottom-Up
A in MTEP20 | B>A | Central | IPL | 17886 | Southeast #8 Breaker Replacement | Replacement of one (1) 138 kV breaker at Southeast, #8 | IN | IN | Reliability need resulting from the annual short circuit analysis as required by NERC TPL-001-4 R2.3 & R2.8 |  |  |  | 2021-12-31 | 2021-12-31 | 138 | 0 | Y |  | Bottom-Up
A in MTEP20 | B>A | Central | IPL | 17887 | Stout South #1A Breaker Replacement | Replacement of one (1) 138 kV breaker at Stout South #1A | IN | IN | Reliability need resulting from the annual short circuit analysis as required by NERC TPL-001-4 R2.3 & R2.8 |  |  |  | 2023-12-31 | 2023-12-31 | 138 | 0 | Y |  | Bottom-Up
A in MTEP20 | B>A | Central | IPL | 17888 | Southport #2 Breaker Replacement | Replacement of one (1) 138 kV breaker at Southport, #2 | IN | IN | Reliability need resulting from the annual short circuit analysis as required by NERC TPL-001-4 R2.3 & R2.8 |  |  |  | 2023-12-31 | 2023-12-31 | 138 | 0 | Y |  | Bottom-Up
A in MTEP20 | B>A | Central | IPL | 18135 | Rockville Auto Replace | Replace 345-138 auto with like-for-like replacement | IN | IN | Age and condition. Part of the IPL TDICS plan. |  |  |  | 2020-12-31 | 2020-12-31 | 345 | 0 | Y |  | Bottom-Up
A in MTEP20 | B>A | Central | IPL | 18138 | Center Substation | Add a total of three new 138 kV breakers and replace three existing 138 kV breakers. | IN | IN | Age and condition. Updates will bring the substation to modern construction and design standards, which will improve worker safety and IPL’s operational flexibility. Part of the IPL TDICS plan. |  |  |  | 2021-12-31 | 2021-12-31 | 138 | 0 | Y |  | Bottom-Up
A in MTEP20 | B>A | Central | NIPS | 16824 | J740 | Interconnection of J740 at NIPSCO's Reynolds 345kV substation | IN | IN | GIA | GIP |  |  | 2021-10-15 | 2021-10-15 | 345 | 0 | Y | 3359403 | Externally Driven
A in MTEP20 | B>A | Central | NIPS | 18274 | Bosserman to Trail Creek | Rebuild Bosserman to Trail Creek | IN | IN | P1 Violation. |  |  |  | 2020-06-01 | 2020-12-01 | 138 | 138 | Y | 12000000 | Bottom-Up
A in MTEP20 | B>A | Central | NIPS | 18276 | Maple to LNG | Rebuild Maple to LNG | IN | IN | N-1-1 (P6) potential violations. Sensitivity Studies show N-1(P1) violations. |  |  |  | 2023-05-01 | 2023-05-01 | 138 | 0 | Y | 18000000 | Bottom-Up
A in MTEP20 | B>A | Central | NIPS | 18278 | LNG to Stillwell | Rebuild LNG to Stillwell line to 1590 ACSR | IN | IN | Potential N-1-1 (P6) Violations. Sensitivity studies show potential N-1 Violations |  |  |  | 2023-05-01 | 2023-05-01 | 138 | 0 | Y | 14000000 | Bottom-Up
A in MTEP20 | B>A | Central | SIGE | 15860 | Broadview 69/12 kV Dist. T2 Repl | Replace 69/12 kV distribution transformer T2 at the Broadview substation | IN | IN | Aging infrastructure (using Vectren's risk model). | Other |  | Age and Condition | 2022-12-31 | 2022-12-31 | 69 | 0 | Y | 1200000 | Bottom-Up
A in MTEP20 | B>A | Central | SIGE | 15940 | East Industrial Trans. Repl. | Replace the 69/12 kV distribution transformer at the East Industrial substation. | IN | IN | Aging infrastructure (using Vectren's risk model). | Other |  | Age and Condition | 2022-12-31 | 2022-12-31 | 69 | 0 | Y | 1200000 | Bottom-Up
A in MTEP20 | B>A | Central | SIGE | 15948 | Fairlawn 69/12 kV Dist. T1 Repl. | Replace the 69/12 kV distribution transformer T1 at the Fairlawn substation. | IN | IN | Aging infrastructure (based on Vectren risk model) | Other |  | Age and Condition | 2022-12-31 | 2022-12-31 | 69 | 0 | Y | 1200000 | Bottom-Up
A in MTEP20 | B>A | Central | SIGE | 15949 | Fuquay 69/12 kV Dist. T1 Repl. | Replace 69/12 kV distribution transformer T1 at the Fuquay substation | IN | IN | Aging infrastructure (based on Vectren risk model) | Other |  | Age and Condition | 2022-12-31 | 2022-12-31 | 69 | 0 | Y | 1200000 | Bottom-Up
A in MTEP20 | B>A | Central | SIGE | 15950 | Hemenway 69/12 kV Dist. T1 Repl. | Replace 69/12 kV distribution transformer T1 at the Hemenway substation | IN | IN | Aging infrastructure (based on Vectren risk model) | Other |  | Age and Condition | 2022-12-31 | 2022-12-31 | 69 | 0 | Y | 1700000 | Bottom-Up
A in MTEP20 | B>A | Central | SIGE | 15952 | Culley 138 kV OCB 2200 2277 Repl. | Replace two 138 kV oil circuit breakers (OCBs) with gas circuit breakers (GCBs). Breaker numbers 2200 and 2277 | IN | IN | Aging infrastructure (based on Vectren risk model) | Other |  | Age and Condition | 2022-12-31 | 2022-12-31 | 138 | 0 | Y | 615000 | Bottom-Up
A in MTEP20 | B>A | Central | SIGE | 15953 | Heidelbach OCB Repl. - 2177 2277 | Replace two 138 kV oil circuit breakers (OCBs) with gas circuit breakers (GCBs) at the Heidelbach station - breaker numbers 2177 & 2277. | IN | IN | Aging infrastructure (based on Vectren risk model) | Other |  | Age and Condition | 2022-12-31 | 2022-12-31 | 138 | 0 | Y | 615000 | Bottom-Up
A in MTEP20 | B>A | Central | SIGE | 15958 | Rockport 69/12 kV T2 Repl. | Replace 69/12 kV distribution transformer T2 at the Rockport substation | IN | IN | Aging infrastructure (based on Vectren risk model) | Other |  | Age and Condition | 2022-12-31 | 2022-12-31 | 69 | 12 | Y | 1700000 | Bottom-Up
A in MTEP20 | B>A | Central | SIGE | 15960 | St. Phillips 69/12 kV T1 Repl. | Replace 69/12 kV distribution transformer T1 at the St. Phillips substation | IN | IN | Aging infrastructure (based on Vectren risk model) | Other |  | Age and Condition | 2022-12-31 | 2022-12-31 | 69 | 12 | Y | 1200000 | Bottom-Up
A in MTEP20 | B>A | Central | SIGE | 15961 | Y31-1 NW - ORS 69 kV Rebuild | Rebuild ~2.1 miles of 69 kV overhead transmission between the Northwest and Ohio River Station substations (line Y31-1). | IN | IN | Aging infrastructure (based on Vectren risk model) | Other |  | Age and Condition | 2022-12-31 | 2022-12-31 | 69 | 0 | Y | 1930000 | Bottom-Up
A in MTEP20 | B>A | Central | SIGE | 15987 | Berry Plastics Dist. XFMR Repl. | Replace one of the distribution transformers serving Berry Plastics. (PSP project) | IN | IN | Aging infrastructure (based on Vectren risk model) | Other |  | Age and Condition | 2024-12-31 | 2024-12-31 | 69 | 0 | Y | 1100000 | Bottom-Up
A in MTEP20 | B>A | Central | SIGE | 18268 | Grandview Generation Interconnect | Installation of Interconnection Facilities and Network Upgrades for generation interconnection project J783 at the Grandview 69 kV substation. | IN | IN | Generation interconnection (J783) |  |  |  | 2021-04-01 | 2021-04-01 | 69 | 0 | Y | 1017496 | Bottom-Up
A in MTEP19 | B>A | Central | DEI | 15757 | West Lafayette Airport Substation | West Lafayette Airport Substation: Add 138/12kv sub in the 13820 circuit | IN | IN | Distribution load growth | Other |  | Load Growth | 2020-06-01 | 2020-06-01 | 138 | 12 | Y | 950000 | Bottom-Up
A in MTEP19 | B>A | Central | DEI | 15760 | J446 Gen. Interconnect | J446 Clinton Wind Farm - Gen. Interconnect: 23010 ckt. - 145MW Wind farm; 3-breaker ring | IN | IN | J446 Gen Queue - IA executed | GIP |  |  | 2020-12-31 | 2020-12-31 | 230 | 0 | Y | 7579786 | Externally Driven
A in MTEP19 | B>A | Central | DEI | 15765 | Brownstown Switching Station 69kV Ring Bus | Brownstown Switching Station 69kV Ring Bus: install (4) breaker ring bus | IN | IN | The assets being addressed in this project fall under one or more of the system programs as outlined in TDSIC Plan filed with Indiana Utility Regulatory Commission on 12/7/2015. | Other |  | Other Local Needs | 2020-12-31 | 2020-12-31 | 69 | 0 | Y | 3770000 | Bottom-Up
A in MTEP19 | B>A | Central | DEI | 15766 | 34517 Structural Improvements | Columbus to Bedford 34517 Structural Improvements: install 8 self-supporting steel intermediate dead-end structures | IN | IN | The assets being addressed in this project fall under one or more of the system programs as outlined in TDSIC Plan filed with Indiana Utility Regulatory Commission on 12/7/2015. | Other |  | Other Local Needs | 2020-12-31 | 2020-12-31 | 345 | 0 | Y | 4000000 | Bottom-Up
A in MTEP19 | B>A | Central | DEI | 15767 | Staunton 230kV Ring Bus | Staunton 230kV Ring Bus: install (3) breaker ring bus | IN | IN | The assets being addressed in this project fall under one or more of the system programs as outlined in TDSIC Plan filed with Indiana Utility Regulatory Commission Exhibit 3-B - Substation Programs Summary. | Other |  | Other Local Needs | 2020-12-31 | 2020-12-31 | 230 | 0 | Y | 10440000 | Bottom-Up
A in MTEP19 | B>A | Central | DEI | 15770 | WVPA Brookston 69/12kV Sub | WVPA Brookston 69/12kV Sub and 69kV source lines | IN | IN | WVPA distribution load growth | Other |  | Load Growth | 2020-06-01 | 2021-06-01 | 69 | 12 | Y | 2338207 | Bottom-Up
A in MTEP19 | B>A | Central | DEI | 15779 | Bedford 345 Ring Bus Expansion | Bedford 345 Ring Bus Expansion - add 2 breakers; replace/upgrade 345/138 Bk 5 to address P2 contingency - can't lose both 34517 and Bk 7 together | IN | IN | Separates Banks 5 and 7 from the 34506 and 34521 lines to increase operating flexibility and reliability of the transformers. | Other |  | Reliability | 2021-12-31 | 2021-12-31 | 345 | 138 | Y | 5000000 | Bottom-Up
A in MTEP19 | B>A | Central | DEI | 15816 | Marathon Petroleum 69kV Sub | Marathon Petroleum 69kV Sub: tap the 6938 ckt to feed new customer sub | IN | IN | Distribution load growth | Other |  | Load Growth | 2019-06-01 | 2019-06-01 | 69 | 0 | Y | 250000 | Bottom-Up
A in MTEP19 | B>A | Central | DEI | 15820 | WVPA Jackson Township 69/12kV Sub | WVPA Jackson Township 69/12kV Sub and 69kV source lines | IN | IN | WVPA distribution load growth | Other |  | Load Growth | 2020-03-31 | 2020-06-01 | 69 | 12 | Y | 10600000 | Bottom-Up
A in MTEP19 | B>A | Central | DEI | 15829 | Greenfield 69/12kV Sub | Greenfield 69/12kV Sub: build new sub to replace existing Greendfield sub with similar source configuration to existing via the 69166 and 6962 ckts | IN | IN | Distribution load growth | Other |  | Load Growth | 2020-12-31 | 2020-12-31 | 69 | 12 | Y | 250000 | Bottom-Up
A in MTEP19 | B>A | Central | DEI | 15834 | Mitchell Lehigh 138/12kV Sub | Mitchell Lehigh 138/12kV Sub: new sub in the 13822 ckt with ATO | IN | IN | Distribution load growth - large new customer load | Other |  | Load Growth | 2021-07-01 | 2021-07-01 | 138 | 12 | Y | 10000000 | Bottom-Up
A in MTEP19 | B>A | Central | DEI | 15835 | Delphi Wells St. 69kV Ring Bus | Delphi Wells St. 69kV Ring Bus: 5 breaker positions | IN | IN | The assets being addressed in this project fall under one or more of the system programs as outlined in TDSIC Plan filed with Indiana Utility Regulatory Commission on 12/7/2015. | Other |  | Other Local Needs | 2020-12-31 | 2020-12-31 | 69 | 0 | Y | 6360000 | Bottom-Up
A in MTEP19 | B>A | Central | DEI | 15840 | Tetersburg 69/12kV Sub | Tetersburg 69/12kV Sub: install new sub in the 69191 ckt | IN | IN | Distribution load growth | Other |  | Load Growth | 2020-06-01 | 2020-06-01 | 69 | 12 | Y | 707000 | Bottom-Up
A in MTEP19 | B>A | Central | DEI | 15927 | WVPA Parke Co. 34.5kV Conversion | WVPA Parke Co. 34.5kV Conversion to 69kV: extend new 69204 ckt (established on MTEP 13849) from Clinton to Carbon West and reconfigure 6905 ckt. | IN | IN | WVPA plan to increase reliability to several 34kV substations | Other |  | Reliability | 2020-06-01 | 2021-12-31 | 69 | 12 | Y | 100000 | Bottom-Up
A in MTEP19 | B>A | Central | DEI | 16364 | WVPA Avon North 138/12kV Sub | WVPA to build 138/12 sub and 138kV looped lines in the 13853 ckt. between Brownsburg and Avon East | IN | IN | WVPA distribution load growth | Other |  | Load Growth | 2019-12-31 | 2019-12-31 | 138 | 12 | Y | 4830000 | Bottom-Up
A in MTEP19 | B>A | Central | DEI | 16384 | WVPA 69130 Loop | WVPA to build / rebuild 69130 line sections to loop feed McCordsville and Lee Hanna 69/12kV subs | IN | IN | 69kV supply line reliability improvement to two WVPA substations | Other |  | Reliability | 2021-06-01 | 2021-06-01 | 69 | 0 | Y | 7030000 | Bottom-Up
A in MTEP19 | B>A | Central | DEI | 16404 | WVPA Enterprise South 69/12kV Sub | WVPA to build 69/12 sub and 69kV tap line from the 6943 ckt. along with a new N.O. alternate feed from WVPA Anson N. in the 69186 ckt. | IN | IN | WVPA distribution load growth | Other |  | Load Growth | 2020-12-31 | 2020-12-31 | 69 | 12 | Y | 11570000 | Bottom-Up
A in MTEP19 | B>A | Central | NIPS | 16084 | J351 Network Upgrades | Network Upgrades necessary for J351 Generating Facility to interconnect at NIPSCO's Stillwell 345kV substation. | IN | IN | Network Upgrades necessary for J351 Generating Facility to interconnect at NIPSCO's Stillwell 345kV substation. | GIP | Shared |  | 2020-03-31 | 2020-03-31 | 345 | 0 | Y | 6692900 | Externally Driven
A in MTEP19 | B>A | Central | NIPS | 16085 | J513 Network Upgrades | Network Upgrades necessary for J513 to connect to Reynolds 138kV as stated in the GIA. | IN | IN | Network Upgrades necessary for J513 to connect to Reynolds 138kV as stated in the GIA. | GIP | Not Shared |  | 2020-08-15 | 2020-08-15 | 138 | 0 | Y | 7874504 | Externally Driven
A in MTEP19 | B>A | Central | NIPS | 16444 | J643 Network Upgrades | J643 Network Upgrades. 138kV Interconnection Ring bus substation. | IN | IN | Generator Interconnection. | GIP |  |  | 2021-09-01 | 2021-09-01 | 138 | 0 | Y | 8921164 | Externally Driven
A in MTEP19 | B>A | Central | SIGE | 15821 | Civic Center UG Exits Replacement | Replace two 69 kV underground circuit exits, ~0.5 miles each. | IN | IN | Aging infrastructure. | Other |  | Age and Condition | 2020-12-31 | 2021-12-31 | 69 | 0 | Y | 2750000 | Bottom-Up
A in MTEP19 | B>A | Central | SIGE | 15823 | Civic Center T2 Repl. | Replace Civic Center 69/12 kV distribution transformer #2 | IN | IN | Aging infrastructure (from Vectren risk model). | Other |  | Age and Condition | 2021-12-31 | 2021-12-31 | 69 | 0 | Y | 1650000 | Bottom-Up
A in MTEP19 | B>A | Central | SIGE | 15851 | Dubois 138/69 kV T2 Repl. | Replace 138/69 kV 100 MVA transformer T2 at Dubois station with new 100 MVA unit | IN | IN | Aging infrastructure (using Vectren's risk model). | Other |  | Age and Condition | 2020-12-31 | 2020-12-31 | 138 | 0 | Y | 2720000 | Bottom-Up
A in MTEP19 | B>A | Central | SIGE | 15853 | Givens 69/12 kV Dist. T2 Repl. | Replace 69/12 kV distribution transformer T2 at the Givens Rd. substation | IN | IN | Aging infrastructure (using Vectren's risk model). | Other |  | Age and Condition | 2021-12-31 | 2021-12-31 | 69 | 0 | Y | 1200000 | Bottom-Up
A in MTEP19 | B>A | Central | SIGE | 15854 | Grimm Rd. 138/12 kV Dist. T2 Repl. | Replace 138/12 kV distribution transformer T2 at the Grimm Rd. substation | IN | IN | Aging infrastructure (using Vectren's risk model). | Other |  | Age and Condition | 2021-12-31 | 2021-12-31 | 138 | 0 | Y | 1200000 | Bottom-Up
A in MTEP19 | B>A | Central | SIGE | 15855 | Pelzer 69 kV OCB Repl - 177 277 188 | Replace three 69 kV oil circuit breakers at the Pelzer station (breakers 177, 277, and 188) | IN | IN | Aging infrastructure (using Vectren's risk model). | Other |  | Age and Condition | 2021-12-31 | 2021-12-31 | 69 | 0 | Y | 500000 | Bottom-Up
A in MTEP19 | B>A | Central | SIGE | 15856 | Northeast 138 kV OCB Repl. - 2126 2188 2288 | Replace three 138 kV oil circuit breakers at the Northeast substation | IN | IN | Aging infrastructure (using Vectren's risk model). | Other |  | Age and Condition | 2021-12-31 | 2021-12-31 | 138 | 0 | Y | 900000 | Bottom-Up
A in MTEP19 | B>A | Central | SIGE | 15857 | St. Wendell 69/12 kV Dist. T1 Repl. | Replace the 69/12 kV distribution transformer T1 at the St. Wendell substation | IN | IN | Aging infrastructure (using Vectren's risk model). | Other |  | Age and Condition | 2021-12-31 | 2021-12-31 | 69 | 0 | Y | 1200000 | Bottom-Up
A in MTEP19 | B>A | Central | SIGE | 15858 | Sunbeam 69/12 kV Dist. T2 Repl. | Replace the 69/12 kV distribution transformer T2 at the Sunbeam substation | IN | IN | Aging infrastructure (using Vectren's risk model). | Other |  | Age and Condition | 2021-12-31 | 2021-12-31 | 69 | 0 | Y | 1200000 | Bottom-Up
A in MTEP19 | B>A | Central | SIGE | 15859 | Tekoppel 69/12 kV T1 & T2 Repl. | Replace both 69/12 kV distribution transformers T1 & T2 at the Tekoppel substation | IN | IN | Aging infrastructure (using Vectren's risk model). | Other |  | Age and Condition | 2021-12-31 | 2021-12-31 | 69 | 0 | Y | 2400000 | Bottom-Up
A in MTEP19 | B>A | Central | SIGE | 15941 | East - West 138 kV Line | Install new 138 kV line from AB Brown to Pigeon Creek to Warrick North substations in order to increase transfer capability and relieve post-contingent loading concerns. First segment (AB Brown - Pigeon Creek) is 13.33 miles and second section (Pigeon Creek - Warrick North) is 23.52 miles, for a total of 36.85 miles. Also includes 1.83 miles of rebuild of existing 69 kV line that will be underbuilt on the 138 kV line. | IN | IN | Increased transfer capability and local reliability. | Other |  | Reliability | 2022-05-01 | 2022-05-01 | 138 | 0 | Y | 42270000 | Bottom-Up
A in MTEP19 | B>A | Central | SIGE | 15943 | Warrick North Cap Banks | Install two new 138 kV Capacitor banks (20 MVAR each) at the Warrick North station for post-contingent voltage support | IN | IN | Local reliability (voltage support) | BRP |  |  | 2023-11-01 | 2023-11-01 | 138 | 0 | Y | 7400000 | Bottom-Up
A in MTEP19 | B>A | Central | SIGE | 15946 | Court St. UG Exits | Replace two existing underground 69 kV circuit exits at the Court St. substation to increase the facility rating (0.21 miles total) | IN | IN | Local reliability | Other |  | Reliability | 2023-11-01 | 2023-11-01 | 69 | 0 | Y | 700000 | Bottom-Up
A in MTEP19 | B>A | Central | SIGE | 15955 | Kings 69/12 kV T1 Repl. | Replace and upgrade 69/12 kV distribution transformer T1 at the Kings substation due to load growth and an existing customer's planned load expansion. | IN | IN | Load growth and customer load expansion | Other |  | Load Growth | 2019-12-31 | 2019-12-31 | 69 | 12 | Y | 1000000 | Bottom-Up
A in MTEP19 | B>A | Central | SIGE | 15957 | Berry 69/12 kV T3 Repl. | Replace and upgrade 69/12 kV transformer at Berry plastics. This transformer is dedicated to Berry Plastics and is being upgraded to accommodate their load expansion. | IN | IN | Customer load expansion | Other |  | Load Growth | 2019-12-31 | 2019-12-31 | 69 | 12 | Y | 1000000 | Bottom-Up
A in MTEP19 | B>A | Central | Vectren | 4395 | NE cap bank tertiary conversion | Remove existing cap banks from the tertiary winding of the 138/69 kV transformer at Northeast sub, and install equivalent cap banks on the 69 kV bus with breakers | IN | IN | To remove old cap banks from the transformer tertiary winding | Other |  | Age and Condition | 2020-12-31 | 2020-12-31 | 69 | 0 | Y | 450000 | Bottom-Up
A in MTEP19 | B>A | Central | Vectren | 4396 | Z71 Scott - Toyota | Install new approx. 13 mile 138 kV line designate Z71 (not Z75). | IN | IN | 138 kV line designate Z71 (not Z75). Provide another 138 kV feed to a large customer (Toyota), provide another path for post contingent flows through the Francisco 345/138 transformer and 138 kV line from Francisco - Elliott (a top congested flowgate), and to provide additional post-continge | Other |  | Reliability | 2021-12-31 | 2021-12-31 | 138 | 0 | Y | 13000000 | Bottom-Up
A in MTEP19 | B>A | Central | Vectren | 4398 | Y52-1 NE - Sunbeam Rebuild | Rebuild and reconductor approx. 3 miles of 69 kV | IN | IN | Aging Infrastructure. | Other |  | Age and Condition | 2019-12-31 | 2019-12-31 | 69 | 0 | Y | 2250000 | Bottom-Up
B in MTEP19 | B | Central | SIGE | 15962 | Court St. OCB 277 Repl. | Replace one 69 kV oil circuit breaker (OCB) with gas circuit breaker (GCB) at the Court St. substation - breaker number 277. | IN | IN | Aging infrastructure (based on Vectren risk model) |  |  |  | 2023-12-31 | 2023-12-31 | 69 | 0 | Y | 175000 | Bottom-Up
B in MTEP19 | B | Central | SIGE | 15964 | Devon 69/12 kV T1 Repl. | Replace 69/12 kV distribution transformer T1 at the Devon substation | IN | IN | Aging infrastructure (based on Vectren risk model) |  |  |  | 2023-12-31 | 2023-12-31 | 69 | 12 | Y | 1250000 | Bottom-Up
B in MTEP19 | B | Central | SIGE | 15965 | Elliott 69 kV OCB Repl. - 400 500 | Replace two 69 kV oil circuit breakers (OCBs) with gas circuit breakers (GCBs) at the Elliott Transmission station | IN | IN | Aging infrastructure (based on Vectren risk model) |  |  |  | 2023-12-31 | 2023-12-31 | 69 | 0 | Y | 350000 | Bottom-Up
B in MTEP19 | B | Central | SIGE | 15966 | Folz Rd. 69/12 kV T1 Repl. | Replace 69/12 kV distribution transformer T1 at the Folz Rd. substation | IN | IN | Aging infrastructure (based on Vectren risk model) |  |  |  | 2023-12-31 | 2023-12-31 | 69 | 12 | Y | 1250000 | Bottom-Up
B in MTEP19 | B | Central | SIGE | 15967 | Jasper Main 69 kV OCB 177 | Replace one 69 kV oil circuit breaker (OCB) with gas circuit breaker (GCB) at the Jasper Main substation - breaker number 177. | IN | IN | Aging infrastructure (based on Vectren risk model) |  |  |  | 2023-12-31 | 2023-12-31 | 69 | 0 | Y | 175000 | Bottom-Up
B in MTEP19 | B | Central | SIGE | 15968 | Northwest 69 kV OCB 277 | Replace one 69 kV oil circuit breaker (OCB) with a gas circuit breaker (GCB) at the Northwest substation - breaker number 277. | IN | IN | Aging infrastructure (based on Vectren risk model) |  |  |  | 2023-12-31 | 2023-12-31 | 69 | 0 | Y | 175000 | Bottom-Up
B in MTEP19 | B | Central | SIGE | 15969 | Oakland City 69 kV OCB 277 | Replace one 69 kV oil circuit breaker (OCB) with a gas circuit breaker (GCB) at the Oakland City substation - breaker number 277. | IN | IN | Aging infrastructure (based on Vectren risk model) |  |  |  | 2023-12-31 | 2023-12-31 | 69 | 0 | Y | 175000 | Bottom-Up
B in MTEP19 | B | Central | SIGE | 15970 | Ohio River 69 kV OCB 4800 | Replace one 69 kV oil circuit breaker (OCB) with a gas circuit breaker (GCB) at the Ohio River Station - breaker number 4800. | IN | IN | Aging infrastructure (based on Vectren risk model) |  |  |  | 2023-12-31 | 2023-12-31 | 69 | 0 | Y | 175000 | Bottom-Up
B in MTEP19 | B | Central | SIGE | 15971 | Ohio River 69/12 kV T1 Repl. | Replace the 69/12 kV distribution transformer T1 at the Ohio River Station. | IN | IN | Aging infrastructure (based on Vectren risk model) |  |  |  | 2023-12-31 | 2023-12-31 | 69 | 12 | Y | 1750000 | Bottom-Up
B in MTEP19 | B | Central | SIGE | 15972 | Perry 69/12 kV T1 Repl. | Replace the 69/12 kV distribution transformer T1 at the Perry Township substation | IN | IN | Aging infrastructure (based on Vectren risk model) |  |  |  | 2023-12-31 | 2023-12-31 | 69 | 12 | Y | 1250000 | Bottom-Up
B in MTEP19 | B | Central | SIGE | 15973 | PPG 69 kV OCB 177 | Replace one 69 kV oil circuit breaker (OCB) with a gas circuit breaker (GCB) at the PPG substation - breaker number 177. | IN | IN | Aging infrastructure (based on Vectren risk model) |  |  |  | 2023-12-31 | 2023-12-31 | 69 | 0 | Y | 175000 | Bottom-Up
B in MTEP19 | B | Central | SIGE | 15974 | St. Henry 69 kV OCB 177 277 | Replace two 69 kV oil circuit breakers (OCBs) with gas circuit breakers (GCBs) at the St. Henry switching station - breaker numbers 177 & 277. | IN | IN | Aging infrastructure (based on Vectren risk model) |  |  |  | 2023-12-31 | 2023-12-31 | 69 | 0 | Y | 350000 | Bottom-Up
B in MTEP19 | B | Central | SIGE | 15975 | Stringtown 69/12 kV T2 Repl. | Replace 69/12 kV distribution transformer T2 at the Stringtown substation. | IN | IN | Aging infrastructure (based on Vectren risk model) |  |  |  | 2023-12-31 | 2023-12-31 | 69 | 12 | Y | 1250000 | Bottom-Up
B in MTEP19 | B | Central | SIGE | 15977 | Sunbeam 69/12 kV T1 Repl. | Replace the 69/12 kV distribution transformer T1 at the Sunbeam substation | IN | IN | Aging infrastructure (based on Vectren risk model) |  |  |  | 2023-12-31 | 2023-12-31 | 69 | 12 | Y | 1250000 | Bottom-Up
B in MTEP19 | B | Central | SIGE | 15978 | Wadesville 69/12 kV T1 Repl. | Replace the 69/12 kV distribution transformer T1 at the Wadesville substation | IN | IN | Aging infrastructure (based on Vectren risk model) |  |  |  | 2023-12-31 | 2023-12-31 | 69 | 12 | Y | 1750000 | Bottom-Up
B in MTEP19 | B | Central | SIGE | 15979 | Winslow 69 kV OCB 377 | Replace one 69 kV oil circuit breaker (OCB) with a gas circuit breaker (GCB) at the Winslow switching station - breaker number 377. | IN | IN | Aging infrastructure (based on Vectren risk model) |  |  |  | 2023-12-31 | 2023-12-31 | 69 | 0 | Y | 175000 | Bottom-Up
B in MTEP19 | B | Central | SIGE | 15980 | Y35 Kings - Oakland City 69 kV Rebuild | Rebuild ~13.2 miles of 69 kV line between Kings and Oakland City substations (line Y35) | IN | IN | Aging infrastructure (based on Vectren risk model) |  |  |  | 2023-12-31 | 2023-12-31 | 69 | 0 | Y | 10300000 | Bottom-Up
B in MTEP19 | B | Central | SIGE | 15982 | Y68/77 Castle - Lynnville Meter 69 kV Rebuild | Rebuild ~4.8 miles of 69 kV line between the Castle and Lynnville Meter stations | IN | IN | Aging infrastructure (based on Vectren risk model) |  |  |  | 2023-12-31 | 2023-12-31 | 69 | 0 | Y | 4000000 | Bottom-Up
B in MTEP19 | B | Central | SIGE | 15983 | Z85-2 Grimm - Angel Mounds 138 kV Rebuild | Rebuild ~3.2 miles of 138 kV line between Grimm Rd. and Angel Mounds substations (line Z85-2). | IN | IN | Aging infrastructure (based on Vectren risk model) |  |  |  | 2023-12-31 | 2023-12-31 | 138 | 0 | Y | 3000000 | Bottom-Up
B in MTEP19 | B | Central | SIGE | 15984 | Broadview 69 kV Loop | Provide second feed (a loop feed) into the 69 kV Broadview substation to increase reliability. (PSP Project) | IN | IN | Local reliability |  |  |  | 2024-12-31 | 2024-12-31 | 69 | 0 | Y | 1610000 | Bottom-Up
B in MTEP19 | B | Central | SIGE | 15985 | Eastland Sub 69 kV Loop | Build second feed (create loop feed) into the Eastland 69 kV substation. (PSP project) | IN | IN | Local reliability |  |  |  | 2024-12-31 | 2024-12-31 | 69 | 0 | Y | 2700000 | Bottom-Up
B in MTEP19 | B | Central | SIGE | 15988 | Cato 138/69 kV T1 Repl. | Replace the 138/69 kV transformer T1 at the Cato substation. (PSP project) | IN | IN | Aging infrastructure (based on Vectren risk model) |  |  |  | 2024-12-31 | 2024-12-31 | 138 | 69 | Y | 2720000 | Bottom-Up
B in MTEP19 | B | Central | SIGE | 15989 | Heidelbach 138/69 kV T1 Repl. | Replace the 138/69 kV transformer T1 at the Heidelbach substation. (PSP project) | IN | IN | Aging infrastructure (based on Vectren risk model) |  |  |  | 2024-12-31 | 2024-12-31 | 138 | 69 | Y | 3710000 | Bottom-Up
B in MTEP19 | B | Central | SIGE | 15991 | Mt. Vernon 138/69 kV T3 Repl. | Replace 138/69 kV transformer T3 at the Mt. Vernon substation. (PSP project) | IN | IN | Aging infrastructure (based on Vectren risk model) |  |  |  | 2024-12-31 | 2024-12-31 | 138 | 69 | Y | 2720000 | Bottom-Up
B in MTEP19 | B | Central | SIGE | 15992 | Mulberry 69 kV T5 Repl. | Replace the 69 kV network transformer T5 at the Mulberry substation. (PSP project) | IN | IN | Aging infrastructure (based on Vectren risk model) |  |  |  | 2024-12-31 | 2024-12-31 | 69 | 0 | Y | 1500000 | Bottom-Up
B in MTEP19 | B | Central | SIGE | 15994 | Newtonville 138/69 kV T2 Repl. | Replace the 138/69 kV transformer T2 at the Newtonville substation. (PSP project) | IN | IN | Aging infrastructure (based on Vectren risk model) |  |  |  | 2024-12-31 | 2024-12-31 | 138 | 69 | Y | 2720000 | Bottom-Up
B in MTEP19 | B | Central | SIGE | 15995 | Newtonville 161/138 kV T3 Repl. | Replace the 161/138 kV transformer T3 at the Newtonville substation. (PSP project) | IN | IN | Aging infrastructure (based on Vectren risk model) |  |  |  | 2024-12-31 | 2024-12-31 | 161 | 138 | Y | 2720000 | Bottom-Up
B in MTEP19 | B | Central | SIGE | 15997 | Stendal 69/12 kV T1 Repl. | Replace the 69/12 kV distribution transformer T1 at the Stendal substation. (PSP project) | IN | IN | Aging infrastructure (based on Vectren risk model) |  |  |  | 2024-12-31 | 2024-12-31 | 69 | 12 | Y | 1500000 | Bottom-Up
B in MTEP19 | B | Central | SIGE | 15998 | Vigo 69/12 kV T1 Repl. | Replace the 69/12 kV distribution transformer T1 at the Vigo substation. (PSP project) | IN | IN | Aging infrastructure (based on Vectren risk model) |  |  |  | 2024-12-31 | 2024-12-31 | 69 | 12 | Y | 1500000 | Bottom-Up
B in MTEP19 | B | Central | SIGE | 15999 | Z84 Duff - Dubois Pole Replacement | Replace poles for ~2.7 miles on the 138 kV line between Duff and Dubois substations (Z84-2). (PSP project) | IN | IN | Aging infrastructure (based on Vectren risk model) |  |  |  | 2024-12-31 | 2024-12-31 | 138 | 0 | Y | 970000 | Bottom-Up
B in MTEP19 | B | Central | SIGE | 16000 | Z84-3 Pole Replacements Duff - IPL | Replace poles for ~19.6 miles on the 138 kV line between the Duff and IPL Petersburg substations. (PSP project) | IN | IN | Aging infrastructure (based on Vectren risk model) |  |  |  | 2024-12-31 | 2024-12-31 | 138 | 0 | Y | 5250000 | Bottom-Up
A in MTEP20 | B>A | Central | BREC | 18012 | Hardinsburg Upgrade | Add a 161 kV breaker and upgrade protection equipment | KY | KY | Increase reliability by adding a breaker between the two parallel transformers. |  |  |  | 2023-06-01 | 2023-06-01 | 161 | 0 | Y | 980000 | Bottom-Up
A in MTEP20 | B>A | Central | BREC | 18071 | Reid and Reid EHV Capacitor Re-Size | Re-size two existing capacitors by replacing the cans with larger cans. | KY | KY | Voltage Support |  |  |  | 2019-10-01 | 2019-10-01 | 161 | 0 | Y | 300000 | Bottom-Up
A in MTEP19 | B>A | Central | BREC | 17765 | New Brandenburg Steel Mill Load Interconnection | Construct a 345 kV station (Redmon Road) to allow connection to the LG&E Mill Creek to Hardin County 345 kV circuit; construct a new 345/161 kV substation (Otter Creek); construct a 2 mile 345 kV circuit from Redmon Rd to Otter Creek; construct a new 9 mile 161 kV circuit from Meade County Substation to Otter Creek; construct a new substation at the steel mill site (Brandenburg Steel Mill); construct a new 9 mile 345 kV circuit from Otter Creek to Brandenburg Steel Mill. | KY | KY | Service for 200 MW load addition. | Other |  | Load Growth |  |  | 345 | 34 | Y | 80000000 | Bottom-Up
A in MTEP20 | B>A | South | CLECO | 17784 | Pelican&Lorgin_Subs | Tap the existing Many to Mansfield 138 kV line 3 miles North of Many substation. Build a 3.1 mile in and out of the tap point to a new 138 kV substation Loring to serve new load. Also tap the existing Many to Mansfield 138 kV line 9 miles south of Mansfield 138 kV substation and build a new Pelican 138 kV substation to serve new Load. | LA | LA | New customer requires 138 kV interconnection for two plants in North East Louisiana |  |  |  | 2020-10-01 | 2020-10-01 | 138 | 13.2 | Y | 24500000 | Bottom-Up
A in MTEP20 | B>A | South | Entergy-LA | 15568 | Oak Grove 138kV : Add Breaker | Install transmission breakers at the existing Oak Grove 138 kV substation, located on the Willow Glen to Gonzales 138 kV transmission circuit. | LA | LA | Enhanced Transmission Reliabiilty. Installation of transmission breakers on the Willow Glen to Gonzales 138 kV circuit will help to improve substation reliability for all of the customers along this transmission circuit which serves more than 10,000 customers. |  |  |  | 2021-12-01 | 2021-12-01 | 138 | 0 | Y | 1874871 | Bottom-Up
A in MTEP20 | B>A | South | Entergy-LA | 15645 | Nelson 138 kV: Install transmission breakers | Nelson – Lake Charles Bulk 138 kV L-654 should be re-terminated at the open bay east of Nelson to Deridder bay and L-698 should be moved to the bay L-654 currently occupies. Breaker 7920 and one new IPO breaker (3000A continuous rating, 80 kA interrupting rating) would be needed to re-terminate L-654 in double-bus-double-breaker scheme. | LA | LA | NERC TPL-001-4 Reliability Standards and Entergy's Planning Guidelines. Internal breaker fault on Nelson 138 kV breaker B7985 results in thermal violation on Nelson to Lake Charles Bulk (L-654) beginning in 2021 summer in MISO MTEP19 cases. |  |  |  | 2022-06-01 | 2022-06-01 | 230 | 0 | Y | 5528302 | Bottom-Up
A in MTEP20 | B>A | South | Entergy-LA | 18136 | Scott to Lafayette 69 kV: Upgrade Station Equipment | Upgrade all station equipment to achieve a through path rating of 588 Amps. | LA | LA | NERC TPL-001-4 Reliability Standards and Entergy's Planning Guidelines P2.2 bus fault at Cecilia 138 kV causes overloads on the Scott to Lafayette 69 kV line |  |  |  | 2021-06-01 | 2021-06-01 | 69 | 0 | Y | 50000 | Bottom-Up
A in MTEP20 | B>A | South | Entergy-LA | 18146 | Sherwood Forest 115 kV: Install breakers | Install transmission line breakers at the existing Sherwood Forest 115 kV substation. | LA | LA | Enhanced Reliability. The installation of 115 kV breakers at the Sherwood Forest substation will reduce exposure to customers to a fault on the transmission line. |  |  |  | 2022-12-01 | 2022-12-01 | 115 | 0 | Y | 5164494 | Bottom-Up
A in MTEP20 | B>A | South | Entergy-LA | 18225 | Washington Parish RIP: Adams Creek To Franklinton 230 kV | Build ~13 miles of new 230 kV line from Adams Creek to Franklinton with a minimum through-path rating of 1600 A Install a 400 MVA 230/115 kV autotransformer at Franklinton Install breakers at Franklinton | LA | LA | Numerous TPL events (P2.1, P2.2, P2.3) overload Amite to Chickenfarm 115 kV and Chickenfarm to Holton 115 kV, they also cause low voltage at Franklinton 115 kV, Pinecliff 115 kV, Chickenfarm 115 kV, and Holton 115 kV. |  |  |  | 2023-06-01 | 2023-06-01 | 230 | 115 | Y | 59499955 | Bottom-Up
A in MTEP20 | B>A | South | Entergy-LA | 18227 | Norris Road 138 kV: New Distribution Station | New distribution station to be cut into the CLECO Youngsville to Segura 138 kV line. | LA | LA | Area Load growth |  |  |  | 2024-06-01 | 2024-06-01 | 138 | 0 | Y | 40851264 | Bottom-Up
A in MTEP20 | B>A | South | Entergy-LA | 18230 | Swartz to Alto 115 kV: Rebuild Line | Rebuild the Swartz to Alto 115 kV line to a minimum of 259 MVA. | LA | LA | NERC TPL-001-4 Reliability Standards and Entergy's Planning Guidelines. P1.2 Loss of the Dunn to Winnsboro 115kV line overloads the Swartz to Alto 115 kV line. |  |  |  | 2024-06-01 | 2024-06-01 | 115 | 0 | Y | 22493744 | Bottom-Up
A in MTEP20 | B>A | South | Entergy-LA | 18233 | Start 115 kV: Construct New Substation | Build new 115 kV substation named Start along with 2 miles of in-and-out 115 kV line from Alto to new substation site. | LA | LA | Load Growth. Continued load growth in the towns of Rayville and Start along I-20 corridor is resulting in low voltage and loss of load. |  |  |  | 2024-06-01 | 2024-06-01 | 115 | 0 | Y | 38674629 | Bottom-Up
A in MTEP20 | B>A | South | LAFA | 14105 | Bonin 69kV Reconfiguration | A reconfiguration of the Bonin 69kV station. | LA | LA | To replace old bus, relays, and breakers as well as improve safety of maintenance and operations. |  |  |  | 2021-09-30 | 2021-09-30 | 69 | 0 | Y | 6400000 | Bottom-Up
A in MTEP19 | B>A | South | AXLA | 17104 | Twin Bridges Auto Replacement | Replace existing Twin Bridges 230/138 kV autotransformer | LA | LA | Project is to replace the autotransformer due to age of the autotransformer | Other |  | Age and Condition | 2020-03-01 | 2020-03-01 | 230 | 138 | Y | 4300000 | Bottom-Up
A in MTEP19 | B>A | South | CLECO | 15914 | Plaisance-Champagne Reconductor | Rebuild Cleco's portion of Plaisance to Champagne 138 kV line (9.5 miles) to 230 kV standards with bundled 954 Cardinal ACSS/TW/HS285. | LA | LA | This line overloads as high as 111.5% in the summer of 2020 MTEP 18 models for loss of P3 Cocodrie to Ville Platte 230 kV line and Acadia Power Block 1. Additionally there are several other contingencies involving the 230 kV line section between Cocodrie and Wells in the future models beyond 2020 Summer peak. | BRP |  |  | 2021-12-01 | 2021-12-01 | 138 | 0 | Y | 9361390 | Bottom-Up
A in MTEP19 | B>A | South | CLECO | 15918 | Manuel Reactor | Add a 9 ohm reactor at Manuel substation in series with the Coughlin to Manuel 138 kV line. Install a by-pass breaker to allow for the Reactor to be by-passed under certain operational conditions. | LA | LA | Coughlin to Manuel 138 kV line overload in the MTEP18 Summer 2020 model for P3 loss of Cocodrie to Ville Platte 230 kV line and Acadia Power Block 1. Additionally in further out years the Manuel to Eunice and Eunice to Richard 138 kV line overload for the same P3 contingency. | BRP |  |  | 2021-06-01 | 2021-06-01 | 138 | 0 | Y | 1462470 | Bottom-Up
A in MTEP19 | B>A | South | CLECO | 15929 | Rapides Breaker Upgrade | Upgrade Breaker 9106 Bushing CT's | LA | LA | Rapides to Rodemacher 230 kV line overloads for the Loss of P3 Coughlin Unit 7 and Rodemacher to Sherwood 230 kV line in the MTEP18 2020, 2023, 2028 Summer Peak and 2023 Winter Peak models. | BRP |  |  | 2020-04-01 | 2020-04-01 | 230 | 0 | Y | 200000 | Bottom-Up
A in MTEP19 | B>A | South | CLECO | 17045 | Sellers Road Expansion | Expand Sellers Road Substation to add a 4 terminal 138 kV substaiton tapped into and out of the Habetz to Flanders 138 kV line near Sellers Road substation. Add a 500 MVA 230/138 kV Auto connecting the existing 230 kV sub to the New 138 kV Sub. | LA | LA | P6 contingency of the Moril to Leblanc 138 kV and the Meaux 230-138 kV Auto or the Meaux to Sellers Road 230 kV line causes the Scott to Judice 138 kV to overload beyond 125% (21W) P6 Contingency of the Meaux 230-138 kV Auto or Meaux to Sellers Road 230 kV line and the Segura to Sellers Road 230 kV line causes the Scott to Judice 138 kV line to overload beyond 125% P6 Loss of the Sellers Road to Meaux 230 kV line or the Meaux 230-138 kV Auto and the Scott to Judice 138 kV line overloads the Moril to Delcambre 138 kV line beyond 125% P2.2 Moril 138 kV bus fault or P2.3 internal breaker fault at Moril causes the Meaux to Abbeville 138 kV line to overload. P6 Loss of Sellers Road to Segura 230 kV and Youngsville to Flanders 138 kV causes multiple facilities to overload over 125% | BRP | Not Shared |  | 2021-12-01 | 2021-12-01 | 230 | 138 | Y | 14130337 | Bottom-Up
A in MTEP19 | B>A | South | Entergy-LA | 12124 | Bogalusa 230-115 kV AT2: Upgrade Auto | Upgrade the line bay bus, line trap and air break switch to a minimum of 2000 Amp rating. | LA | LA | P2.3 Breaker Failure contingency at Bogalusa 230 kV causes a thermal violation on the Bogalusa AT2. Upgrading the station equipment will increase the thermal rating in order to alleviate the thermal violation. | BRP |  |  | 2019-06-14 | 2019-06-14 | 230 | 0 | Y | 131759 | Bottom-Up
A in MTEP19 | B>A | South | Entergy-LA | 12139 | Jefferson Parish Area Reliability Plan Phase 2 | Construct a new 230 kV substation named Munster located north of the existing Meraux Substation. The new substation will be configured as a 9 breaker, breaker and a half substation. The substation will be cut in to the existing Meraux to Michoud, Meraux to Oaks, and Michoud to Arabi 230 kV transmission lines. Approximately, one mile of double circuit 230kV transmission line will be installed, with a minimum through-path rating of 1608 Amperes, from the new Munster Substation to the point at which the existing 230kV turns north towards the Michoud Substation. The terminations at the junction point will be reconfigured to accommodate the new installation. | LA | LA | The P6 N-1-1 Loss of Peters Road to Behrman 230 kV line along with Michoud to Meraux 230 kV line will overload multiple facilities as the 115 kV system in the area attempts to support the 230 kV system, primarily through the Behrman 230-115 kV autotransformer. | BRP |  |  | 2022-06-01 | 2022-06-01 | 230 | 0 | Y | 53318000 | Bottom-Up
A in MTEP19 | B>A | South | Entergy-LA | 12744 | Cotton 230 kV: Construct New Substation | Construct new distribution substation in southwest Ouachita Parish to serve area load. | LA | LA | The area distribution network experiences an inability to serve area load as a result of various transformer and feeder area contingencies. The area also experiences low voltages due to the distance of the feeders during the peak hours of the year. | Other |  | Load Growth | 2021-06-01 | 2021-06-01 | 230 | 0 | Y | 16900000 | Bottom-Up
A in MTEP19 | B>A | South | Entergy-LA | 13956 | Goos Ferry 230 kV: New Substation | Goos Ferry substation with high side breakers will cut in on the Gillis to Chalkley 230 kV line section. | LA | LA | Distribution System Load Growth. | Other |  | Load Growth | 2022-06-01 | 2022-06-01 | 230 | 0 | Y | 21200000 | Bottom-Up
A in MTEP19 | B>A | South | Entergy-LA | 13985 | Henry 69 kV: New Line and Substation | Henry 69 kV substation will cut in and out of the Five Points to Line 281 Tap 69 kV line section. There will be additional 69 kV line built from the cut in point to the new station depending on its location. | LA | LA | Distribution System Load Growth. | Other |  | Load Growth | 2022-06-01 | 2022-06-01 | 69 | 0 | Y | 21900000 | Bottom-Up
A in MTEP19 | B>A | South | Entergy-LA | 15566 | Addis to Tiger 230 kV Series Reactor | Install a 230kV five ohm reactor on the existing Addis to Tiger 230kV line. | LA | LA | The 2018 MISO Deliverability study shows an overload on the Addis to Tiger 230 kV line for the P1.2 loss of the Dow Meter to Chenango 230 kV or the Richardson to Iberville 230 kV line in 2023. | BRP |  |  | 2023-06-01 | 2023-06-01 | 230 | 0 | Y | 16230999 | Bottom-Up
A in MTEP19 | B>A | South | Entergy-LA | 15569 | Port Hudson to Blount 69 kV: Upgrade Switches | Upgrade substation equipment which is currently de-rating the conductor on this circuit. | LA | LA | The P2.1 loss of Port Hudson to Zachary REA Tap 69 kV will overload from Dixie Baker to Baker to Blount 69kV. The P2.1 loss of the Blount to Baker 69 kV line will overload the Zachary to Dixie Baker 69 kV line. | Other |  | Reliability | 2021-06-01 | 2021-06-01 | 69 | 0 | Y | 3900000 | Bottom-Up
A in MTEP19 | B>A | South | Entergy-LA | 15584 | Champagne to Plaisance 138 kV: Rebuild to 230 kV (operate at 138 kV) | Rebuild Champagne to Plaisance 138kV line to 230 kV specifications and operate at 138 kV. Entergy and CLECO own portions of this line. | LA | LA | NERC TPL-001-4 Reliability Standards and Entergy's Planning Guidelines drive this project. Multiple CLECO contingencies involving the path between Cocodrie and West Fork(P1.2, P2.1, and P2,2's) will cause overloads on the 138kV Champagne to Plaisance line. | BRP |  |  | 2021-06-01 | 2021-06-01 | 138 | 0 | Y | 9000000 | Bottom-Up
A in MTEP19 | B>A | South | Entergy-LA | 15586 | Ninemile S2015: Close Normally Open Breaker | Return breaker S2015 to it’s normally closed operating condition. | LA | LA | Return Ninemile to it's intended configuration to increase reliability. The breaker is currently operated open due to the impact of the breaker failure which will be mitigated by other projects planned to be in service. | Other |  | Reliability | 2020-06-01 | 2020-06-01 | 230 | 0 | Y | 0 | Bottom-Up
A in MTEP19 | B>A | South | Entergy-LA | 15587 | Adams Creek 230 kV: Add Breaker | Add a redundant 230 kV breaker at Adams Creek 230 kV substation. | LA | LA | NERC TPL-001-4 and Entergy Planning Criteria drive this project. P2.3 internal breaker fault will overload the Adams Creek to Bogalusa 230 kV line circuit 2. | BRP |  |  | 2021-06-01 | 2021-06-01 | 230 | 0 | Y | 900000 | Bottom-Up
A in MTEP19 | B>A | South | Entergy-LA | 15600 | Lower Coast 230kV : Add Breaker | Install transmission breakers at the existing Lower Coast 230 kV substation, located on the Behrman to Kaiser 230 kV transmission circuit. | LA | LA | Enhanced Transmission Reliabiilty. Installation of transmission breakers on the Behrman to Kaiser 230 kV circuit will help to improve substation reliability for all of the customers along this transmission circuit which serves more than 10,000 customers. | Other |  | Reliability | 2021-06-30 | 2021-06-30 | 230 | 0 | Y | 2141252 | Bottom-Up
A in MTEP19 | B>A | South | Entergy-LA | 15602 | Move Nesser Normally Open Point | Create a new normally open point by closing Switch 20647 and opening Switch 20648. Nesser will be served from a Tap on the Tiger to East line rather than the Harelson to Jonescreek line. Include as part of this project the upgrade of any facilities that would limit the Tiger to East 69 kV line to less than 975 Amperes. | LA | LA | Entergy's Planning Guidelines. Open breaker contingency at Coly to Lockhart 69 kV causes a thermal violation on the Harelson to Line 372 Tap 69 kV line. | Other |  | Reliability | 2021-06-01 | 2021-06-01 | 69 | 0 | Y | 1720000 | Bottom-Up
A in MTEP19 | B>A | South | Entergy-LA | 15603 | Coly to DEMCO Coly 69 kV Upgrade | Upgrade Coly to DEMCO Coly 69 kV through path ratings for circuit 1 and circuit 2. | LA | LA | Entergy's Planning Guidelines. The P0 thermal overload on the Coly to DEMCO Coly 69 kV Ckts 1 and 2. | Other |  | Reliability | 2021-06-01 | 2021-06-01 | 69 | 0 | Y | 1840000 | Bottom-Up
A in MTEP19 | B>A | South | Entergy-LA | 15626 | Colyell Creek 230 kV: New Substation | Construct a new 230 kV distribution station on the French Settlement to Springfield 230 kV line section. The new station will be near the French Settlement 230 kV station. | LA | LA | Distribution load growth | Other |  | Load Growth | 2021-12-01 | 2021-12-01 | 230 | 0 | Y | 26128997 | Bottom-Up
A in MTEP19 | B>A | South | Entergy-LA | 16045 | New Orleans Power Station Interconnection Project | Install breakers, jumpers, and all other station work at Michoud 115 kV to accommodate the interconnection of the New Orleans Power Station. | LA | LA | Station work associated with the interconnection of the New Orleans Power Station at the Michoud 115 kV bus. | GIP |  |  | 2020-02-28 | 2020-02-28 | 115 | 0 | Y | 9350000 | Externally Driven
A in MTEP19 | B>A | South | Entergy-LA | 16544 | Riverview 138 kV: New Customer Station | Entergy is proposing to construct a new 138 kV substation (Riverview 138 kV Substation) which will serve an existing customer’s ~5 MW load. The industrial load is currently being served on distribution facilities sourcing from the Cohen 230 kV station. The new substation will be located in Port Allen, LA west of LA Highway 1 and south of Catalyst Drive. The interconnection will cut in and out of the existing 138 kV line between Wilbert and Louisiana Station. The customer has agreed to fully fund the project and transfer the 138 kV facilities upon completion to Entergy. | LA | LA | Customer driven station | Other |  | Load Growth | 2019-04-09 | 2019-04-09 | 138 | 0 | Y | 0 | Bottom-Up
A in MTEP19 | B>A | South | Entergy-LA | 16566 | J683 Interconnection: Construct 138 kV Switching Substation | Construct a 138 kV 3 breaker ring bus on the Wilbert to Livonia 138 kV line. | LA | LA | This new 138kV 3 breaker ring bus is needed to accommodate the J683 Solar Facility. | GIP |  |  | 2020-10-30 | 2020-10-30 | 138 | 0 | Y | 2300000 | Externally Driven
A in MTEP19 | B>A | South | Entergy-LA | 16570 | J581 Interconnection: Construct 115 kV Switching Station | Construct a 115kV 3 breaker ring bus on the Sterlington - Bastrop 115kV line section. | LA | LA | The 3 breaker ring bus 115kV switching station is needed to interconnect the J581 facility. | GIP |  |  | 2021-12-31 | 2021-12-31 | 115 | 0 | Y | 8125000 | Externally Driven
A in MTEP19 | B>A | South | Entergy-LA | 16571 | Galion 115 kV: Install Transmission Line Bay and Breakers (J544 Interconnection) | Install transmission circuit breakers at the Galion 115kV substation. | LA | LA | Circuit breakers at the Galion substation are required for the interconnection of J544. | GIP |  |  | 2021-09-15 | 2021-09-15 | 115 | 0 | Y | 6468000 | Externally Driven
A in MTEP19 | B>A | South | Entergy-LA | 17044 | Sellers Leblanc Project (SLP) | o Construct the new Sellers Road to Conrad 230 kV line (operate at 138 kV). Approximately 19.2 miles based on preliminary routing. o Reroute the existing Gecko to Cecelia 69 kV line (to facilitate the 230 kV line construction). o Add a 138 kV line breaker, switches, bus, etc at the Conrad Substation. o Add a 138 kV series reactor at the Cecelia 138 kV Substation on the line to Bonin. | LA | LA | P2.4 internal breaker fault on the Scott 138 kV bus tie causes the Bonin to Cecelia to overload. P2.2 Scott 138 kV Bus fault causes the Bonin to Cecelia 138 kV to overload. P6 contingency of the Moril to Leblanc 138 kV and the Meaux 230-138 kV Auto or the Meaux to Sellers Road 230 kV line causes the Scott to Judice 138 kV to overload beyond 125% (21W) P6 Contingency of the Meaux 230-138 kV Auto or Meaux to Sellers Road 230 kV line and the Segura to Sellers Road 230 kV line causes the Scott to Judice 138 kV line to overload beyond 125% P6 Loss of the Sellers Road to Meaux 230 kV line or the Meaux 230-138 kV Auto and the Scott to Judice 138 kV line overloads the Moril to Delcambre 138 kV line beyond 125% P2.2 Moril 138 kV bus fault or P2.3 internal breaker fault at Moril causes the Meaux to Abbeville 138 kV line to overload. P6 Loss of Sellers Road to Segura 230 kV and Youngsville to Flanders 138 kV causes multiple facilities to overload over 125% | BRP | Not Shared |  | 2020-12-01 | 2021-12-01 | 138 | 0 | Y | 69900000 | Bottom-Up
A in MTEP19 | B>A | South | Entergy-LA | 17606 | Ponchatoula 230 kV: Add Breakers and Transfer Bus | Entergy is proposing to add line breakers and a transfer bus at the existing Ponchatoula 230 kV substation in South Louisiana. Ponchatoula 230 kV station currently does not contain transmission breakers or a transfer bus. | LA | LA | This project will reduce exposure to the large amount of customers served from the Ponchatoula 230 kV station to a line fault. This project also addresses operational concerns and provides flexibility during planned and unplanned outages. | Other |  | Reliability | 2021-12-01 | 2021-12-01 | 230 | 0 | Y | 5200000 | Bottom-Up
A in MTEP19 | B>A | South | Entergy-LA | 17608 | Michigan 230 kV Substation: Cut in Nelson to Manena 230 kV | Entergy is proposing to cut the new Nelson to Manena 230 kV line, project ID# 10008, in and out of the Michigan 230 kV station. | LA | LA | This project will reduce exposure to customers served in the area on the 230 kV system. This project also addresses operational concerns and provides flexibility during planned and unplanned outages. | Other |  | Reliability | 2020-12-01 | 2020-12-01 | 230 | 0 | Y | 10600000 | Bottom-Up
B in MTEP20 | B | South | Entergy-LA | 18228 | Golden Meadow to Clovelly 115 kV: Rebuild line | Rebuild the ~7 mile Golden Meadow to Clovelly 115 kV line to 230 kV specifications. | LA | LA | Enhanced Reliability. The P1.3 loss of the Barataria 230/115 kV autotransformer creates loadings on Clovelly to Golden Meadow over 90%. Increase reliability to the area. |  |  |  | 2029-06-01 | 2029-06-01 | 115 | 0 | Y | 47170000 | Bottom-Up
B in MTEP20 | B | South | Entergy-LA | 18229 | Lake Charles Bulk 230-138 kV Autotransformer | Construct a 230 kV 3 breaker ring bus at Lake Charles Bulk. Cut in the Gillis to Chalkley 230 kV line. Install a 230-138 kV Autotransformer at Lake Charles Bulk similar to the Nelson 230-138 kV Autotransformer | LA | LA | NERC TPL-001-4 Reliability Standards and Entergy's Planning Guidelines P1.2 loss of the Nelson to Lake Charles 138 kV L698 overloads the Nelson to Lake Charles Bulk 138 kV L654 and vice versa. |  |  |  | 2029-06-01 | 2029-06-01 | 230 | 138 | Y | 27820000 | Bottom-Up
B in MTEP20 | B | South | Entergy-LA | 18236 | Winnsboro to Gilbert 115 kV: Rebuild Line | Rebuild Winnsboro to Gilbert 115 kV line to a minimum of 259 MVA. The line will be built using a double circuit configuration but only strung on one side. The unused side will be reserved for a future 230 kV line. | LA | LA | Enhanced Reliability. High thermal loading on the Winnsboro to Redgum 115 kV lines under N-1 system conditions. |  |  |  | 2028-06-01 | 2028-06-01 | 115 | 0 | Y | 18005207 | Bottom-Up
B in MTEP20 | B | South | Entergy-LA | 18247 | Gilbert to Wisner 115 kV: Rebuild Line | Rebuild Gilbert to Wisner 115 kV line to a minimum of 259 MVA. The line will be built using a double circuit configuration but only strung on one side. The unused side will be reserved for a future 230 kV line. | LA | LA | Enhanced Reliability. High thermal loading on the Winnsboro to Redgum 115 kV lines under N-1 system conditions. |  |  |  | 2029-06-01 | 2029-06-01 | 115 | 0 | Y | 10652871 | Bottom-Up
B in MTEP20 | B | South | Entergy-LA | 18252 | Wisner to Metropolis 115 kV: Rebuild Line | Rebuild Wisner to Metropolis 115 kV line to a minimum of 259 MVA. The line will be built using a double circuit configuration but only strung on one side. The unused side will be reserved for a future 230 kV line. | LA | LA | Enhanced Reliability. High thermal loading on the Winnsboro to Redgum 115 kV lines under N-1 system conditions. |  |  |  | 2029-06-01 | 2029-06-01 | 115 | 0 | Y | 4873667 | Bottom-Up
B in MTEP20 | B | South | Entergy-LA | 18253 | Metropolis to Red Gum 115 kV: Rebuild Line | Rebuild Metropolis to Red Gum 115 kV line to a minimum of 259 MVA. The line will be built using a double circuit configuration but only strung on one side. The unused side will be reserved for a future 230 kV line. | LA | LA | Enhanced Reliability. High thermal loading on the Winnsboro to Redgum 115 kV lines under N-1 system conditions. |  |  |  | 2030-06-01 | 2030-06-01 | 115 | 0 | Y | 43743862 | Bottom-Up
B in MTEP19 | B | South | Entergy-LA | 15570 | Erath Tap to Leblanc 69 kV: Upgrade line | Upgrade the 69kV line segment between Erath tap and Leblanc tap 69kV. | LA | LA | Baseline Reliability. The P2.1 loss of Leblanc to Moril 69kV line segment will overload Erath tap to Leblanc tap |  |  |  | 2026-12-01 | 2026-12-01 | 69 | 0 | Y | 3000000 | Bottom-Up
B in MTEP19 | B | South | Entergy-LA | 15589 | Golden Meadow to Barataria 115 kV: Rebuild line to 230 kV specifications (operate at 115 kV) | This project proposes to re-build the entire 31 mile Barataria – Golden Meadow (172.0) 115 kV line to 230 kV construction initially operated at 115 kV, utilizing 954 ACSS. | LA | LA | Enhanced reliability. The replacement of this aging infrastructure will increase reliability in the area. |  |  |  | 2027-06-01 | 2027-06-01 | 115 | 0 | Y | 96100000 | Bottom-Up
B in MTEP19 | B | South | Entergy-LA | 15595 | Joliet to Southport 230 kV: Upgrade Line | Rebuild existing Southport to Joliet 230kV line. | LA | LA | In 2028 summer the P2.3 Internal Breaker Fault of a Ninemile breaker will cause overloads on the Southport to Joliet 230kV line. |  |  |  | 2028-06-01 | 2028-06-01 | 230 | 0 | Y | 8724876 | Bottom-Up
B in MTEP19 | B | South | Entergy-LA | 15599 | Almonaster to Curran 230 kV: Upgrade Line | Rebuild existing Almonaster to Curran 230kV line. | LA | LA | In 2028 summer the P2.3 Internal Breaker Fault of at Ninemile will cause overloads on the Almonaster to Curran 230 kV line. |  |  |  | 2028-06-01 | 2028-06-01 | 230 | 0 | Y | 24500000 | Bottom-Up
B in MTEP19 | B | South | Entergy-LA | 15604 | Bosco 138 kV Series reactor: Place reactor in service | Operate the Bosco series reactor normally in service. | LA | LA | NERC TPL-001-4 Reliability Standards and Entergy's Planning Guidelines. The P1.2 loss of the Richard to Wells 500 kV line results in a thermal overload on the Richard to Colonial Academy to Acadia to Scanlan 138 kV lines. |  |  |  | 2028-06-01 | 2028-06-01 | 138 | 0 | Y | 0 | Bottom-Up
B in MTEP19 | B | South | Entergy-LA | 15605 | Frisco-Tezcuco 230kV: Upgrade Circuit 1 and 2 | Increase the rating of the Tezcuco to Frisco 230 circuit #1 and #2 to a minimum of 1925A (765 MVA). | LA | LA | MISO identified thermal overloads on the Tezcuco to Frisco circuit #1 and #2 during their MTEP18 Deliverability Analysis. • Tezcuco to Frisco 230kV circuit #1 following the loss of Tezcuco to Frisco 230kV circuit #2 • Tezcuco to Frisco 230kV circuit #2 following the loss of Tezcuco to Frisco 230kV circuit #1 |  |  |  | 2023-06-01 | 2023-06-01 | 230 | 0 | Y | 2620000 | Bottom-Up
B in MTEP19 | B | South | Entergy-LA | 15654 | Delhi - Tallulah 115 kV rebuild | Rebuild 20.8 miles of 115kV line from Delhi to Tallulah with a minimum through-path rating of 259 MVA (1300A). Operate the series reactor at Delhi as normally open to mitigate thermal overloads observed on the Winnsboro to Red Gum 115kV line sections. | LA | LA | NERC TPL-001-4 Reliabiilty Standards and Entergy's Local Planning Criteria. The P3 loss of the Baxter Wilson - Perryville 500 kV line coupled with the loss of Grand Gulf generation results in thermal overloads on the Delhi - Tallulah and Winnsboro - Gilbert 115 kV line sections. |  |  |  | 2027-06-01 | 2027-06-01 | 115 | 0 | Y | 27000000 | Bottom-Up
B in MTEP19 | B | South | Entergy-LA | 15656 | Urania - New 115 kV substation | Build 1 mile of new 115kV “In and Out” T-line from Standard/Jena line to the newly purchased site. Build 115kV high side bus in accordance with Entergy Transmission and Substation standards to accommodate one new 50 MVA, 115/34.5kV transformer and one new 40 MVA 69/13.8 kV transformer. Include appropriate high-side fault protection. Install 21.6 MVAR cap bank at new Urania substation. | LA | LA | High distribution loads in the area are driving the need for a new 115 kV substation. Load shifts to the new substation will drive violations of NERC TPL-001-4 Reliabiilty Standards and Entergy's Local Planning Criteria. P2 for the loss of Standard substation. mitigation involves the installation of a 20.4 MVAR capbank. |  |  |  | 2025-06-01 | 2025-06-01 | 115 | 0 | Y | 25200000 | Bottom-Up
A in MTEP20 | B>A | West | ATC | 4727 | Winona - Atlantic (Winona69) 69kV, rebuild | Rebuild Winona - Atlantic (Winona69) 69kV line with new structures and T2-477 conductor | MI | MI | Reliability, SBRM |  |  |  | 2024-12-31 | 2024-12-31 | 69 | 0 | Y | 30400000 | Bottom-Up
A in MTEP20 | B>A | West | ATC | 18020 | Mackinac HVDC SCM Layer Asset Renewal | Mackinac HVDC SCM Layer Asset Renewal | MI | MI | Asset Renewal - Substation |  |  |  | 2022-12-31 | 2022-12-31 | 345 | 0 | Y | 4000000 | Bottom-Up
A in MTEP20 | B>A | East | CETO | 17990 | CE Substation Equipment Replacement Program - 2022 | Replace damaged or defective substation equipment with new equipment | MI | MI | Replace substation equipment that is defective, damaged, or fails testing parameters to improve system reliability and address safety concerns |  |  |  | 2022-12-31 | 2022-12-31 | 138 | 0 | Y | 410000 | Bottom-Up
A in MTEP20 | B>A | East | CETO | 17991 | CE Pole & Line Equipment Replacement Program - 2022 | Replace damaged or defective poles, towers, cross arms, insulators, guying, and switches, as needed, to maintain the lines' condition | MI | MI | Replace structures and line equipment that are defective or damaged to maintain line performance, reduce outages, address code clearance, and/or address safety concerns |  |  |  | 2022-12-31 | 2022-12-31 | 138 | 0 | Y | 530000 | Bottom-Up
A in MTEP20 | B>A | East | CETO | 17992 | Hodenpyl Line Rebuild | Rebuild the Hodenpyl 138 kV Line, approximately 0.6 miles, utilizing 138 kV single circuit construction | MI | MI | This line is constructed with towers and copper line conductor that date to the 1920's. Experience with these vintage of towers has shown significant ground level rusting which will lead to tower failure and line outages. |  |  |  | 2021-12-31 | 2021-12-31 | 138 | 0 | Y | 330000 | Bottom-Up
A in MTEP20 | B>A | East | CETO | 17993 | Muskegon #2 Line Rebuild | Rebuild a portion of the Muskegon #2 138 kV Line, approximately 2.1 miles, utilizing 138 kV single circuit construction | MI | MI | This portion of the line is constructed with towers installed in 1928. Experience with these vintage of towers has shown significant ground level rusting which will lead to tower failure and line outages. |  |  |  | 2022-12-31 | 2022-12-31 | 138 | 0 | Y | 1000000 | Bottom-Up
A in MTEP20 | B>A | East | CETO | 17994 | Four Mile-Northridge 138 kV Lines | Construct two new 138 kV lines from Four Mile Substation to the new Northridge Substation | MI | MI | METC has identified a plan to install a new station named Northridge, MISO MTEP#16002. METC's plan will require Consumers Energy to reconnect its Four Mile Substation to the new station with two new transmission lines. |  |  |  | 2022-12-31 | 2022-12-31 | 138 | 0 | Y | 500000 | Bottom-Up
A in MTEP20 | B>A | East | CETO | 18272 | Dort-Mott Lake 138 kV Lines | Construct two new 138 kV lines from Dort Substation to the new Mott Lake Substation | MI | MI | METC has identified a plan to install a new station named Mott Lake, MTEP#18190. METC's plan will require Consumers Energy to reconnect its Dort Substation to the new station with two new transmission lines. |  |  |  | 2024-12-31 | 2024-12-31 | 138 | 0 | Y | 500000 | Bottom-Up
A in MTEP20 | B>A | East | CETO | 18273 | Morrow Relocation 138 kV Lines | Construct two new 138 kV lines from the new Morrow South Substation to METC's new interconnection substation | MI | MI | Consumers Energy plans to relocate and rebuild its distribution assets at Morrow Substation in a location south of the existing substation. This project will require two new transmission lines between the new Morrow South Substation and METC's new interconnection substation, MTEP #18069. |  |  |  | 2022-10-01 | 2022-10-01 | 138 | 0 | Y | 500000 | Bottom-Up
A in MTEP20 | B>A | East | ITCT | 15880 | Navarre - River Rouge 120 kV Rebuild | Rebuild the 2.9 miles of 954 ACSR conductor to 2156 ACSR on the Navarre – River Rouge 120 kV line and upgrade station equipment at both ends. | MI | MI | The Navarre – River Rouge 120 kV circuit is projected to overload for multiple shutdown-plus-contingency that involve the loss of the Adelaide-Ironton-Navarre 120 kV line. The limiting elements on this circuit are the 954 ACSR conductor and equipment at Navarre and River Rouge 120 kV stations. | BRP |  |  | 2025-12-31 | 2025-12-31 | 120 | 0 | Y | 9728000 | Bottom-Up
A in MTEP20 | B>A | East | ITCT | 15883 | Bismarck-Stephens #2 120 kV Rebuild | Rebuild approximately 3.61 miles of 795 ACSS and 954 ACSR conductors to 2156 ACSR on the Bismarck – Stephens #2 120 kV line. | MI | MI | The Bismarck – Stephens #2 120 kV circuit is projected to overload for a shutdown-plus-contingency that takes out two Stephens 345/120kV transformers. The overloaded facilities are the 954 ACSR conductor and station equipment at Stephens 120 kV. | BRP |  |  | 2027-12-31 | 2027-12-31 | 120 | 0 | Y | 9100000 | Bottom-Up
A in MTEP20 | B>A | East | ITCT | 15890 | Pontiac - Walton 120 kV Rebuild | Rebuild approximately 4.8 miles of 477 ACSR X2 and 1431 ACSR conductors from Pontiac to Giddings 2 Tap to Walton using 2156 ACSR. Also, upgrade station equipment at Pontiac 120kV and Walton 120 kV. | MI | MI | The Pontiac to Giddings 2 to Walton 120 kV circuit is projected to overload for a couple shutdown-plus-contingency that involve the loss of Bloomfield – Pontiac 230 kV line. The overloaded facilities are the 477 ACSR X2 and 1431 ACSR conductors along this line and the station equipment at Pontiac and Walton 120 kV. | BRP |  |  | 2025-12-31 | 2025-12-31 | 120 | 0 | Y | 11027000 | Bottom-Up
A in MTEP20 | B>A | East | ITCT | 15900 | Wayne - Newburgh #1 120 kV Rebuild | Rebuild approximately 2.7 miles of 795 ACSS conductor to 2156 ACSS on the Wayne – Newburgh #1 120 kV circuit. Also, upgrade station equipment at both Wayne and Newburgh 120 kV. | MI | MI | The Wayne – Newburgh #1 120 kV circuit is projected to be overloaded for T-1 and other contingency types that involve the loss of Wayne – Newburgh #2 120 kV circuit. The overloaded facilities are the 795 ACSS conductor and equipment at Wayne and Newburgh 120 kV stations. | BRP |  |  | 2025-12-31 | 2025-12-31 | 120 | 0 | Y | 4778000 | Bottom-Up
A in MTEP20 | B>A | East | ITCT | 15959 | Hager - Sunset 120 kV Rebuild | The proposed solution is to rebuild 4.33 miles of the Sunset – Hager 120kV circuit using 1431 ACSR conductor with single circuit steel structures and replace terminal equipment at Hager Pos HD. | MI | MI | The Sunset – Hager 120kV line is projected to overload for a shutdown plus contingency involving the Yost – Otawa 120kV and Hines – Wayne 230kV line. The identified overloaded equipment on this circuit are the conductor and terminal equipment at Hager Pos HD. The thermal violations are found on peak cases. | BRP |  |  | 2026-12-31 | 2026-12-31 | 120 | 0 | Y | 9331000 | Bottom-Up
A in MTEP20 | B>A | East | ITCT | 16015 | Sunset - Quaker 120 kV Rebuild | The proposed solution is to rebuild 0.259 mile of the Sunset – Quaker 120kV circuit using 2156 ACSR conductor with single circuit steel structures and replace terminal equipment and station equipment at Quaker Pos HD and Sunset Pos HN. | MI | MI | The Sunset – Quaker 120kV line is projected to overload for a shutdown plus contingency scenarios, the worst involving the Quaker – Magneto 120kV and Wixom 345/120 kV transformer. The identified overloaded equipment on this circuit are the conductor, terminal equipment and station equipment at Quaker Pos HD and Sunset Pos HN. The thermal violations are found on peak and off peak cases. | BRP |  |  | 2025-12-31 | 2025-12-31 | 120 | 0 | Y | 482000 | Bottom-Up
A in MTEP20 | B>A | East | ITCT | 17124 | Frisbie - Midtown 120kV Cable Relocation | Relocate approximately 1500 ft of underground pipe type cable that is currently under the Milwaukee Street bridge over I-75 in the city of Detroit. | MI | MI | The Michigan Department of Transportation has mandated the cable be removed from the bridge. | Other |  | Other Local Needs | 2021-06-01 | 2021-06-01 | 120 | 0 | Y | 1900000 | Bottom-Up
A in MTEP20 | B>A | East | ITCT | 17364 | J793 Generator Interconnection | ITCT will install a new 345 kV station with 3-345 kV breakers and associated disconnects in a ring bus configuration. ITCT will loop the Belle River - Fitz #2 345kV circuit into the new J793 substation. ITCT will upgrade relay panels at the Fitz and Belle River Power Plant Stations to accommodate the new generator J793. | MI | MI | J793 is a 1175 MW (Summer) / 1209 MW (Winter) combined cycle generating station interconnecting on the ITCT Belle River - Fitz #2 345kV circuit. | GIP |  |  | 2021-05-14 | 2021-05-14 | 345 | 0 | Y | 9734993 | Externally Driven
A in MTEP20 | B>A | East | ITCT | 17504 | Abrams Interconnection | Install a new 120kV substation. Extend the Northeast-Skylark line by adding 0.1 miles of 954 ACSR conductor to loop in Abrams interconnection station. Add three 120kV breakers and two bus sections. | MI | MI | DTE will install two new transformers at the new interconnection station to serve 14MVA of relocated load from DTEs Arsenal and Pluto substations. | Other |  | Load Growth | 2022-11-01 | 2022-11-01 | 120 | 0 | Y | 4519000 | Bottom-Up
A in MTEP20 | B>A | East | ITCT | 17744 | ITCT Customer Interconnections - Year 2023 | Customer interconnection requests and retirements less than $1 million with in service date in year 2023. | MI | MI | Customer Requests are often in need of interconnection on an expedited basis. This blanket allows interconnection requests of smaller nature to be quickly studied and connected by ITC. |  |  |  | 2023-12-31 | 2023-12-31 | 120 | 0 | Y | 2000000 | Bottom-Up
A in MTEP20 | B>A | East | ITCT | 17995 | J752 Network Upgrades | Install Relay and communication cutoff switch at Ringle 345 kV station for the J752 expansion of J161. | MI | MI | Install Relay and communication cutoff switch at Ringle to facilitate the J752 expansion of J161. | GIP |  |  | 2019-09-23 | 2019-09-23 | 345 | 0 | Y | 35000 | Externally Driven
A in MTEP20 | B>A | East | ITCT | 17998 | Stone Pool - Temple 120 kV | The proposed solution is to build a new circuit (approximately 1.25 miles) from the Stone Pool 120 kV Station to the Temple 120 kV station utilizing 3200 Kcmil underground cable. | MI | MI | The Frisbie – Resource and Resource – Alfred 120 kV underground cables are projected to overload for the shutdown plus contingency involving the Caniff – Cyril – Mack and Mack – Northeast 120 kV lines during peak conditions. |  |  |  | 2024-06-01 | 2024-06-01 | 120 | 0 | Y |  | Bottom-Up
A in MTEP20 | B>A | East | ITCT | 17999 | Corktown - Waterman 120 kV UG Re-conductor | The proposed solution is to re-conductor approximately 3.7 miles utilizing 3200 Kcmil underground cable. | MI | MI | The Corktown – Waterman 120 kV underground cable is projected to marginally overload in normal conditions during peak load. |  |  |  | 2024-06-01 | 2024-06-01 | 120 | 0 | Y |  | Bottom-Up
A in MTEP20 | B>A | East | ITCT | 18082 | Apolo Interconnection | Construct a new in-and-out station consisting of a single tie breaker and three straight buses with room for future tie breaker. Install one 120 kV tie breaker, two 120 kV line breakers, buswork, and associated disconnects. Connect two customer owned transformers to the new station. | MI | MI | DTE has requested a new 120 kV interconnection on the ITCT Hunters Creek-Lapeer 120kV circuit. The interconnection request is to feed two DTE transformers, and a future third transformer. |  |  |  | 2022-03-30 | 2022-03-30 | 120 | 0 | Y |  | Bottom-Up
A in MTEP20 | B>A | East | ITCT | 18168 | Bismarck - Red Run 230 kV Reconductor | Reconductor approximately 2 miles utilizing 1431 ACSR and upgrade terminal station equipment at Bismarck and Red Run. | MI | MI | The Bismarck – Red Run 230 kV circuit is projected to overload for the N-1-1 involving the loss of the Northeast – Stephens 230 kV circuit and either the Jewel 345/230 kV transformer, the Sterling 230/120 kV transformer, or the Jewel – Sterling 230 kV circuit during peak conditions. Terminal station equipment at Bismarck and Red Run also become overloaded. |  |  |  | 2024-06-01 | 2024-06-01 | 230 | 0 | Y |  | Bottom-Up
A in MTEP20 | B>A | East | ITCT | 18170 | Diesel – Evergreen 120 kV Rebuild | Rebuild approximately 0.4 miles utilizing 1431 ACSR on double circuit structures and upgrade terminal equipment at Evergreen. | MI | MI | The Diesel – Evergreen 120 kV circuit is projected to become overloaded for the N-1-1 involving the loss of the Sunset – Hager 120 kV circuit and either the Wayne 345/230 kV transformer, the Hines 230/120 kV transformer, or the Hines – Wayne 230 kV circuit during peak conditions. Terminal station equipment at Evergreen also become overloaded. |  |  |  | 2024-06-01 | 2024-06-01 | 120 | 0 | Y |  | Bottom-Up
A in MTEP20 | B>A | East | ITCT | 18173 | Levan – Ottawa 120 kV Rebuild | Rebuild approximately 0.4 miles utilizing 1431 ACSR on double circuit structures and upgrade terminal equipment at Levan and Ottawa. | MI | MI | The Levan – Ottawa 120 kV circuit is projected to become overloaded for the N-1-1 involving the loss of the Sunset – Hager 120 kV circuit and either the Wayne 345/230 kV transformer, the Hines 230/120 kV transformer, or the Hines – Wayne 230 kV circuit during peak conditions. Terminal equipment at Levan and Ottawa also become overloaded. |  |  |  | 2024-06-01 | 2024-06-01 | 120 | 0 | Y |  | Bottom-Up
A in MTEP20 | B>A | East | ITCT | 18175 | Van Dyke 2 – Sloan 120 kV Rebuild | Rebuild approximately 0.6 miles 795 ACSR utilizing 1431 ACSR on double circuit structures and upgrade terminal station equipment at Sloan. | MI | MI | The Van Dyke 2 – Sloan 120 kV circuit is projected to become overloaded for various N-1-1, the worst of which involving the loss of the Northeast – Stephens and Bismarck – Red Run 230 kV circuits during peak conditions. Terminal equipment at Sloan also become overloaded. |  |  |  | 2024-06-01 | 2024-06-01 | 120 | 0 | Y |  | Bottom-Up
A in MTEP20 | B>A | East | ITCT | 18178 | Hancock – Lily 120 kV Rebuild | Rebuild approximately 2 miles of 3/0 Cu X2 utilizing 954 ACSR on double circuit structures. | MI | MI | The Hancock - Lily 120 kV circuit is projected to become overloaded for a P7 (double circuit tower) outage, during peak conditions in MISO’s MTEP19 study. |  |  |  | 2024-06-01 | 2024-06-01 | 120 | 0 | Y |  | Bottom-Up
A in MTEP20 | B>A | East | ITCT | 18179 | Hood – Lily 120 kV Rebuild | Rebuild approximately 2.6 miles of 3/0 Cu X2 utilizing 954 ACSR on double circuit structures. | MI | MI | The Hood – Lily 120 kV circuit is projected to become overloaded for a P7 (double circuit tower) outage, during peak conditions in MISO’s MTEP19 study. |  |  |  | 2024-06-01 | 2024-06-01 | 120 | 0 | Y |  | Bottom-Up
A in MTEP20 | B>A | East | ITCT | 18184 | Red Run – Logan – Sloan 120 kV Rebuild | Rebuild approximately 2.8 miles utilizing 954 ACSR on double circuit structures and upgrade terminal equipment at Sloan. | MI | MI | The Red Run – Logan – Sloan 120 kV circuit is projected to become marginally overloaded for various P6 (N-1-1) outages, during peak conditions in MISO’s MTEP19 study. Terminal equipment at Sloan also become overloaded. |  |  |  | 2024-06-01 | 2024-06-01 | 120 | 0 | Y |  | Bottom-Up
A in MTEP20 | B>A | East | ITCT | 18189 | Brownstown – Trenton Channel #3 120 kV Rebuild | Rebuild approximately 3.6 miles utilizing 2156 ACSR on double circuit structures and upgrade terminal equipment at Brownstown and Trenton Channel 120 kV stations. | MI | MI | The Brownstown – Trenton Channel # 3 120 kV circuit is projected to become overloaded for various P6 contingencies that involve the loss of Brownstown – Trenton Channel #2 120 kV line in MISO’s MTEP19 study. The terminal equipment at Brownstown and Trenton Channel also become overloaded. |  |  |  | 2024-06-01 | 2024-06-01 | 120 | 0 | Y |  | Bottom-Up
A in MTEP20 | B>A | East | ITCT | 18191 | Brownstown – Navarre #2 230 kV Rebuild | Rebuild approximately 14 miles utilizing 2156 ACSR on double circuit structures and upgrade terminal station equipment at Navarre. | MI | MI | The Brownstown – Navarre # 2 230 kV circuit is projected to become overloaded for P1, P2, P3, P7, and P6 outages during shoulder peak conditions in MISO’s MTEP19 study. Terminal equipment at Navarre 230 kV also become overloaded. |  |  |  | 2024-06-01 | 2024-06-01 | 230 | 0 | Y |  | Bottom-Up
A in MTEP20 | B>A | East | ITCT | 18192 | Hines – Levan 120 kV Rebuild | Rebuild approximately 0.5 miles utilizing 2156 ACSR on double circuit structures and upgrade terminal equipment at Hines and Levan stations. | MI | MI | The Hines – Levan circuit is projected to become overloaded for various P6 contingencies during shoulder peak conditions in MISO’s MTEP19 study. |  |  |  | 2024-06-01 | 2024-06-01 | 120 | 0 | Y |  | Bottom-Up
A in MTEP20 | B>A | East | ITCT | 18193 | Zebra – S-Wr-W Tap 120 kV Rebuild | Rebuild approximately 1.2 miles utilizing 954 ACSR on single circuit structures and upgrade terminal equipment at Zebra. | MI | MI | The Zebra – S-Wr-W Tap 120 kV circuit is projected to become marginally overloaded for various P6 outages during shoulder peak conditions in MISO’s MTEP19 study. |  |  |  | 2024-06-01 | 2024-06-01 | 120 | 0 | Y |  | Bottom-Up
A in MTEP20 | B>A | East | ITCT | 18194 | Malta 2 – Grayling 1 120 kV Sag Remediation | Remediate the sag on this 120 kV section to at least 244 MVA for summer emergency rating. | MI | MI | The Malta 2 – Grayling 1 120 kV section is projected to become overloaded for various P6 contingencies involving the loss of Lenox – Sigma 120kV line in both ITCT’s 2019 Assessment and MISO’s MTEP19 studies. |  |  |  | 2023-12-31 | 2023-12-31 | 120 | 0 | Y |  | Bottom-Up
A in MTEP20 | B>A | East | ITCT | 18195 | Superior – S-Wr-W Tap 120 kV Sag Remediation | Remediate the sag on this 120 kV section to at least 256 MVA for summer emergency rating | MI | MI | The 120 kV section from Superior-Willow Run-Wayne (S-WR-W) tap to Superior is projected to become overloaded for a P6 contingency that takes out the Dayton – Collins 120kV circuit and 345/120kV transformer at Coventry. |  |  |  | 2023-12-31 | 2023-12-31 | 120 | 0 | Y |  | Bottom-Up
A in MTEP20 | B>A | East | ITCT | 18196 | Bismarck – Malta 2 120 kV Sag Remediation | Remediate the sag on this 120 kV line up to the conductor’s limit. | MI | MI | The Bismarck – Malta 2 120 kV section is projected to become overloaded for various P6 contingencies involving the loss of Lenox – Sigma 120 kV line in MISO’s MTEP19 study. |  |  |  | 2023-12-31 | 2023-12-31 | 120 | 0 | Y |  | Bottom-Up
A in MTEP20 | B>A | East | ITCT | 18197 | Apache – Seneca 120 kV Sag Remediation Phase 2 | Remediate the sag on this 120 kV line to at least 233 MVA for summer emergency rating. | MI | MI | The Apache – Seneca 120 kV line is projected to become heavily loaded (98%) for various P6 contingencies in MISO’s MTEP19 study. |  |  |  | 2023-12-31 | 2023-12-31 | 120 | 0 | Y |  | Bottom-Up
A in MTEP20 | B>A | East | ITCT | 18198 | Airport – Tulsa 120 kV Sag Remediation | Remediate the sag on this 120 kV line up to the conductor’s limit. | MI | MI | The Airport – Tulsa 120 kV section is projected to become overloaded for various P6 contingencies involving the loss of the Brownstown 345/120kV transformer #301 in both ITCT’s 2019 Assessment and MISO’s MTEP19 studies. |  |  |  | 2023-12-31 | 2023-12-31 | 120 | 0 | Y |  | Bottom-Up
A in MTEP20 | B>A | East | ITCT | 18199 | Venoy – A-B-VN Tap 120 kV Sag Remediation | Remediate the sag on this 120 kV section to at least 250 MVA for summer emergency rating. | MI | MI | The 120 kV section from Allison-Brock-Venoy (A-B-VN) Tap to Venoy is projected to become marginally overloaded for various P6 contingencies involving the loss of Hager – Sunset 120kV line in both ITCT’s 2019 Assessment and MISO’s MTEP19 studies. |  |  |  | 2023-12-31 | 2023-12-31 | 120 | 0 | Y |  | Bottom-Up
A in MTEP20 | B>A | East | ITCT | 18200 | Hemphill – Hunters Creek 120 kV Sag Remediation | Remediate the sag on this 120 kV line up to the conductor’s limit. | MI | MI | The Hemphill – Hunters Creek 120 kV line is projected to become overloaded for various P6 contingencies in MISO’s MTEP19 study. |  |  |  | 2023-12-31 | 2023-12-31 | 120 | 0 | Y |  | Bottom-Up
A in MTEP20 | B>A | East | ITCT | 18201 | Hunters Creek – Stratford 120 kV Sag Remediation | Remediate the sag on this 120 kV line to at least 175 MVA for summer emergency rating. | MI | MI | The Hunters Creek – Stratford 120 kV line is projected to become overloaded for P6 contingency that takes out both 345/120kV transformers at Pontiac in MISO’s MTEP19 study. |  |  |  | 2023-12-31 | 2023-12-31 | 120 | 0 | Y |  | Bottom-Up
A in MTEP20 | B>A | East | ITCT | 18202 | Navarre 2nd 230/120kV Transformer | Install a second 230/120kV transformer at Navarre station. | MI | MI | Multiple sections of the two 120 kV path from Trenton Channel to Riverview are projected to become overloaded under various P6 contingencies involving the loss of the Navarre 230/120kV transformer. These same contingencies also cause numerous low voltages in the area, including buses at and near Trenton Channel, Riverview, River Rouge, Ironton, and more. The thermal and voltage violations are identified in both ITCT’s 2019 Assessment and MISO’s MTEP19 studies. |  |  |  | 2023-12-31 | 2023-12-31 | 230 | 120 | Y |  | Bottom-Up
A in MTEP20 | B>A | East | ITCT | 18203 | Sterling 120 kV Station Equipment Upgrade | Upgrade station equipment at Sterling 120 kV station. | MI | MI | The 120 kV bus-ties at Sterling are projected to become heavily overloaded for various P6 contingencies, mostly involving the loss of Chestnut – Sterling 120 kV line, in both ITCT’s 2019 Assessment and MISO’s MTEP19 studies. |  |  |  | 2023-12-31 | 2023-12-31 | 120 | 0 | Y |  | Bottom-Up
A in MTEP20 | B>A | East | ITCT | 18204 | Brownstown – Trenton Channel #2 120 kV Station Equipment Upgrade | Upgrade the station equipment at Trenton Channel 120 kV position “HH”. | MI | MI | The Brownstown – Trenton Channel #2 120 kV line is projected to become overloaded for several P6 contingencies that involve the loss of Brownstown – Trenton Channel #3 120 kV circuit in both ITCT’s 2019 Assessment and MISO’s MTEP19 studies. |  |  |  | 2023-12-31 | 2023-12-31 | 120 | 0 | Y |  | Bottom-Up
A in MTEP20 | B>A | East | ITCT | 18205 | Red Run 120 kV Station Equipment Upgrade | Upgrade the station equipment at Redrun 120 kV station. | MI | MI | The 120 kV bus-tie at Red Run is projected to become overloaded for various P6 contingencies in both ITCT’s 2019 Assessment and MISO’s MTEP19 studies. The P6 contingencies that cause this thermal violation include combinations of these outages: Jewell – Sterling 230 kV, Northeast – Stephens 230 kV, Northeast 230/120 kV transformer, Jewell 345/230kV transformer, Stephens 345/230kV transformer. |  |  |  | 2023-12-31 | 2023-12-31 | 120 | 0 | Y |  | Bottom-Up
A in MTEP20 | B>A | East | ITCT | 18237 | 2023 ITCTransmission Asset Replacement Program | Replace aging and outdated equipment at a pace that will insure each type of equipment is replaced near its projected end of life. | MI | MI | Replace aging and outdated equipment on a cycle that will ensure each piece of equipment is replaced near its expected end of life. Modern equipment can improve reliability, use state of the art technology, and typically will allow for longer maintenance intervals. New equipment is also commonly equipped with better monitoring and alarming functionality giving improved remote supervision. All of this will help to reduce overall maintenance costs. The Asset Replacement program includes a variety of replacement programs for several types of equipment including but not limited to: • Circuit Breakers/switchers • Protective equipment (relays/control) • DC battery and charging systems • Surge Arresters • Instrument Transformers • Disconnect Switches • Wood poles • Miscellaneous line equipment (insulators, cross-arms, etc.) |  |  |  | 2023-12-31 | 2023-12-31 | 345 | 120 | Y | 28315000 | Bottom-Up
A in MTEP20 | B>A | East | ITCT | 18240 | Boyne 120 kV Capacitor | Low voltage is projected to occur at the Golf 120 kV, Houston 120 kV, and Macomb 120 kV buses for shutdown plus contingency scenarios involving a DTE transformer in surround area plus either the Macomb – Staphens 120 kV line or the Golf – Bismarck 120 kV line. The low voltage violations were identified in the 2020, 2023, and 2028 peak and off-peak load models. | MI | MI | Install 54 MVAR (3x18 MVAR) capacitor at Boyne 120 kV station to maintain acceptable voltage levels within this region of the Oakland area. |  |  |  | 2023-12-31 | 2023-12-31 | 120 | 0 | Y |  | Bottom-Up
A in MTEP20 | B>A | East | ITCT | 18241 | Stephens Transformer 303 Replacement | Replace Stephens 345/120kV Transformer #303 with a new transformer. | MI | MI | The transformer is at the end of its life. A detailed project justification document will be uploaded as soon as it's available. |  |  |  | 2023-12-31 | 2023-12-31 | 345 | 120 | Y | 4800000 | Bottom-Up
A in MTEP20 | B>A | East | ITCT | 18242 | Wayne Transformer 303 Replacement | Replace Wayne 345/120kV Transformer #303 with a new transformer. | MI | MI | The transformer has reached the end of it's life. A detailed project justification document will be uploaded as soon as it's available. |  |  |  | 2023-12-31 | 2023-12-31 | 345 | 120 | Y | 4800000 | Bottom-Up
A in MTEP20 | B>A | East | ITCT | 18246 | Wayne 345/120kV Transformer Addition | Install a new 345/120kV transformer at Wayne station. | MI | MI | The Wayne 345/120kV transformer branches are projected to become overloaded for P6 contingencies that take out the Coventry 345/120kV transformer plus either 345/120kV bank at Wayne. |  |  |  | 2023-12-31 | 2023-12-31 | 345 | 120 | Y |  | Bottom-Up
A in MTEP20 | B>A | East | ITCT | 18271 | DIG 230 kV Reconfiguration | Reconfigure Baxter station into a 4-breaker ring bus. Rebuild a total of ~0.8 mile of 230kV lines to 1431 ACSR on double-circuit. Break the DIG-Navarre-Waterman 230kV 3-ended line and bring the Navarre side into DIG GIS 230kV station to form a third outlet. Reconfigure the connections at DIG Sub. 42 and Sub 48/49 so that transformers #M & T48 are tapped off of the Baxter-DIG 230kV line, and transformers N and T49 to be directly fed from Baxter 230kV station. Also, install a second 230/120kV transformer at Waterman. | MI | MI | The loss or outage of one of the two 230kV connections into DIG will cause the other one to become overloaded. A shutdown-plus-contingency will completely drop over 700 MW of generation and all the loads within this (DIG) site. |  |  |  | 2022-12-31 | 2022-12-31 | 230 | 120 | Y |  | Bottom-Up
A in MTEP20 | B>A | East | ITCT | 18277 | Bloomfield – Upgrade HE Station Equipment | Upgrade the station equipment at Bloomfield 120 kV position “HE”. | MI | MI | The Bloomfield – Ninja (formerly Bloomfield – Hood) 120 kV line is projected to become overloaded for a double-circuit-tower outage (P71) that takes out Pontiac – Placid and Pontiac Wixom 345 kV lines in MISO’s MTEP19 study. |  |  |  | 2022-12-31 | 2022-12-31 | 120 | 0 | Y |  | Bottom-Up
A in MTEP20 | B>A | East | ITCT | 18313 | Bauer - Pontiac Sag Remediation | Raise the sag limit on the 2-954 ACSR 54/7 conductor span to achieve a summer emergency rating of at least 1258 MVA | MI | MI | Projects J717, J728, and J752 cause the Bauer - Pontiac circuit to be overloaded in the 2017 February DPP MI study cycle. Remediate the sag limit to achieve at least a rating of 1258 MVA summer emergency. |  |  |  | 2020-11-13 | 2020-11-13 | 345 | 0 | Y | 961200 | Bottom-Up
A in MTEP20 | B>A | East | METC | 15896 | Battle Creek - Morrow #1 138 kV Rebuild | The proposed solution is to rebuild 19.38 miles from Str #008E57412E to Str #008E8623 of the Battle Creek – Morrow #1 138kV circuit using 954 ACSR conductor with future double-circuit steel structures and leave adjacent side vacant for future circuit and also rebuild 3.3 miles from Str #008E8623 to Morrow station of 477 ACSR conductor to 954 ACSR conductor with double circuit steel structures. In addition, replace station equipment at Morrow station. | MI | MI | The Battle Creek – Morrow #1 138kV circuit is projected to overload for shutdown plus contingency scenarios, the worst involving the Argenta – Battle Creek and Argenta – Tompkin 345kV lines. The identified overloaded equipment on this circuit is the conductors, terminal and station equipment at Morrow station. The thermal violations are found on off peak cases. | BRP |  |  | 2025-06-01 | 2025-06-01 | 138 | 0 | Y |  | Bottom-Up
A in MTEP20 | B>A | East | METC | 15939 | Leoni - Beecher 138 kV Rebuild | The proposed solution is to rebuild 0.21 miles of the Mercer – Cement City Jct. section of the Leoni – Beecher circuit using 954 ACSR conductor with single circuit steel structures. Also remediate sag limit on the 6-wired conductor section to increase its summer emergency rating to a minimum of 1196 Amps (286 MVA). | MI | MI | The Mercer – Cement City Jct. section of the Leoni – Beecher 138kV line is projected to overload for a shutdown plus contingency involving the Custer – Whiting 120kV and Morocco 345/138 kV transformer. The identified overloaded equipment on this circuit is the conductor and sag limit on the six-wired conductor section. The thermal violations are found on peak cases. | BRP |  |  | 2027-12-31 | 2027-12-31 | 138 | 0 | Y | 4300000 | Bottom-Up
A in MTEP20 | B>A | East | METC | 17365 | J717_J728 Generator Interconnection | Build a new 138 kV 3 Breaker ring substation cut in from the Bullock - Warren 138 kV circuit. Install OPGW from the new station to Warren 138 kV sub. | MI | MI | J717 and J728 are a combined 385.4 MW wind farm requesting to share a point of interconnection on the Warren - Bullock 138 kV circuit in the DPP-2017-FEB cycle. | GIP |  |  | 2020-06-30 | 2020-06-30 | 138 | 0 | Y | 8191000 | Externally Driven
A in MTEP20 | B>A | East | METC | 17384 | J796 (Goss) Network Upgrade | Network upgrades required to connect the J796 project. J796 is capable of 239 MW of solar generation. METC's Goss 138kV station will need to be expanded by adding four 138kv breakers to accommodate the interconnection. | MI | MI | Network upgrades are required for the J796 project capable of 239MW of solar generation. | GIP |  |  | 2020-11-20 | 2020-11-20 | 138 | 0 | Y | 2810000 | Externally Driven
A in MTEP20 | B>A | East | METC | 17745 | METC Customer Interconnections - Year 2023 | Customer interconnection requests and retirements less than $1 million with in service dates in the year 2023. | MI | MI | Customer Requests are often in need of interconnection on an expedited basis. This blanket allows interconnection requests of smaller nature to be quickly studied and connected by METC. |  |  |  | 2023-12-31 | 2023-12-31 | 138 | 0 | Y | 2000000 | Bottom-Up
A in MTEP20 | B>A | East | METC | 17844 | Summerton - Bullock cut in to Salt River 138 kV | Extend the Summerton - Bullock 138 kV circuit by extending ~15 miles of double circuit 138 kV construction into Salt River 138 kV station. | MI | MI | The J717 and J728 Generator Interconnections caused a stability issue and several local Thermal overloads. Cutting in the Summerton - Bullock line to the J717 and J728 interconnection station to be named Salt River mitigates the stability issue and eliminates the need for other thermal mitigations. |  |  |  | 2022-10-28 | 2022-10-28 | 138 | 0 | Y | 35493000 | Bottom-Up
A in MTEP20 | B>A | East | METC | 17965 | J806 Network Upgrades | Build a new 138 kV, 3 breaker ring switching station cut in from the METC Rice Creek - Vrooman 138kV circuit. | MI | MI | J806 is a 149 MW Solar Power Plant that requested to interconnect to the METC Rice Creek - Vrooman 138 kV circuit in the DPP-2017-AUG cycle. | GIP |  |  | 2021-10-31 | 2021-10-31 | 138 | 0 | Y | 6561000 | Externally Driven
A in MTEP20 | B>A | East | METC | 17997 | Donaldson Creek Interconnection Phase 2 | Build a new breaker row 13, breakers 13B7 and 13M9 with associated switches and terminate a new WPSC line to Rodgers. | MI | MI | WPSC MTEP17 Appendix A project 12203, 138kV Voltage Conversion, requires two new connections to Donaldson Creek. METC will need to add a 3rd 138kV row to its Donaldson Creek station to terminate a new 138kV interconnection to Rodgers. |  |  |  | 2022-06-01 | 2022-06-01 | 138 | 0 | Y | 1450000 | Bottom-Up
A in MTEP20 | B>A | East | METC | 18000 | Tallmadge - Four Mile 138kV Rebuild | The proposed solution is to rebuild 9.22 miles of the Tallmadge – Four Mile 138kV circuit using 2156 ACSR conductor with double circuit steel structures. Also replace station equipment at Four Mile and Tallmadge substation. | MI | MI | The Tallmadge - Four Mile 138kV circuit is projected to overload for DCT or shutdown plus contingency scenario, the worst involving the Tallmadge - Wealthy 1 and Tallmadge - Wealthy 2 138kV lines. The identified overloaded equipment on this circuit is the conductors and station equipment at Tallmadge and Four Mile stations. The thermal violations are found on peak cases. |  |  |  | 2024-06-01 | 2024-06-01 | 138 | 0 | Y |  | Bottom-Up
A in MTEP20 | B>A | East | METC | 18001 | Keystone 138 kV BM11 Station Eq. Upgrades | The proposed solution is to upgrade terminal station equipment at Keystone position BM11. | MI | MI | Station equipment at Keystone Position BM11 on the Keystone – Gray Rd 138 kV line is projected to overload for various scenarios, the worst involving the loss of the Boardman – Keystone #2 138 kV line and the Gray Road – Keystone 138 kV line. The thermal violations are found in peak conditions. |  |  |  | 2023-12-31 | 2023-12-31 | 138 | 0 | Y |  | Bottom-Up
A in MTEP20 | B>A | East | METC | 18002 | Tippy – Haring Jct. – Wexford 138kV Rebuild | The proposed solution is to rebuild 28.62 miles of the Tippy – Haring Jct. section and 0.01 miles of the Haring Jct. – Warren circuit using 954 ACSR with steel structures and replace terminal equipment at Tippy Hydro. | MI | MI | The Tippy – Haring Jct. – Wexford 138kV circuit is projected to overload for various scenarios, the worst involving the loss of the Keystone – Ludington #1 345 kV line and the Keystone – Tippy Hydro 138 kV line. The identified overloaded equipment on this circuit is the conductor and terminal station equipment at Tippy Hydro. The thermal violations are only found on 85% peak cases. |  |  |  | 2024-06-01 | 2024-06-01 | 138 | 0 | Y |  | Bottom-Up
A in MTEP20 | B>A | East | METC | 18004 | Tanner - Tallmadge 138kV Sag Remediation | The proposed solution is to remediate sag limit on the Tanner - Tallmadge 138kV circuit to increase its summer emergency rating to a minimum of 236 MVA/989 Amps. | MI | MI | The Tanner - Tallmadge 138kV circuit is projected to overload for shutdown plus contingency scenarios, the worst involving the Cobb - Myer 138kV line and Ludington - Pere Marquette 345kV line. The identified overloaded equipment on this circuit is the sag on the Tanner - Tallmadge circuit. The thermal violations are found on peak conditions. |  |  |  | 2023-12-31 | 2023-12-31 | 138 | 0 | Y |  | Bottom-Up
A in MTEP20 | B>A | East | METC | 18005 | Campbell - Port Sheldon 138kV Sag Remediaion | The proposed solution is to completely remediate sag limit on the Campbell - Port Sheldon 138kV circuit to conductor limit. | MI | MI | The Campbell - Port Sheldon 138kV circuit is projected to overload for shutdown plus contingency scenario, the worst involving the Campbell - Tallmadge and Campbell - Roosevelt 345kV lines. The identified overloaded equipment on this circuit is the sag on the Campbell - Port Sheldon circuit. The thermal violations are found on peak and off peak conditions. |  |  |  | 2023-12-31 | 2023-12-31 | 138 | 0 | Y |  | Bottom-Up
A in MTEP20 | B>A | East | METC | 18009 | Regal – Luce 138kV Rebuild | The proposed solution is to rebuild 0.75 mile of the Regal - Luce 138kV circuit using 954 ACSR conductor with double circuit steel structures. | MI | MI | The Regal - Luce 138kV circuit is projected to overload for shutdown plus contingency scenario, the worst involving the Nelson Road - Murphy 345kV line and Redstone - Regal 138kV line. The identified overloaded equipment on this circuit is the conductor on the Regal - Luce circuit. The thermal violations are found on off peak conditions at Ludington pumping condition only. |  |  |  | 2024-06-01 | 2024-06-01 | 138 | 0 | Y |  | Bottom-Up
A in MTEP20 | B>A | East | METC | 18010 | Campbell - Tyler 138kV Sag Remediation | The proposed solution is to completely remediate sag limit on the Campbell - Tyler 138kV circuit to conductor limit. | MI | MI | The Campbell - Tyler 138kV circuit is projected to overload for shutdown plus contingency scenarios, the worst involving the Campbell - Tallmadge and Campbell - Roosevelt 345kV lines. The identified overloaded equipment on this circuit is the sag on the Campbell - Tyler circuit. The thermal violations are found on peak and off peak conditions. |  |  |  | 2023-12-31 | 2023-12-31 | 138 | 0 | Y |  | Bottom-Up
A in MTEP20 | B>A | East | METC | 18040 | Cottage Grove - Karn 138kV Sag Remediation | The proposed solution is to remediate sag limit on the Cottage Grove - Karn 138kV circuit to increase its summer emergency rating to a minimum of 162 MVA (679 Amps). | MI | MI | The Cottage Grove - Karn 138kV circuit is projected to overload for shutdown plus contingency scenario, the worst involving the Livingston - Gallagher - Tittabawassee and Keystone - Ludington 345kV lines. The identified overloaded equipment on this circuit is the sag on the Cottage Grove - Karn circuit. The thermal violations are found on off peak conditions. |  |  |  | 2023-12-31 | 2023-12-31 | 138 | 0 | Y |  | Bottom-Up
A in MTEP20 | B>A | East | METC | 18043 | Scott Lake - Argenta 138kV Sag Remediation | The proposed solution is to remediate sag limit on the Scott Lake - Trowbridge 138kV section to increase its summer emergency rating to a minimum of 219 MVA (917 Amps) and also remediate sag limit on the Trowbridge - Argenta 138kV section to increase its summer emergency rating to a minimum of 235 MVA (985 Amps). | MI | MI | The Scott Lake - Argenta 138kV circuit is projected to overload for shutdown plus contingency scenario, the worst involving the Black River - Campbell and Tyler - Black River 138kV lines. The identified overloaded equipment on this circuit is the sag on the Scott Lake - Argenta circuit. The thermal violations are found on off peak conditions. |  |  |  | 2023-12-31 | 2023-12-31 | 138 | 0 | Y |  | Bottom-Up
A in MTEP20 | B>A | East | METC | 18055 | Riverview Interconnection | Convert METC Riverview substation from a three-breaker straight bus configuration to a six-breaker ring. Install three 138kV breakers, buswork, and associated disconnects. | MI | MI | Consumers Energy has provided notification for a new 138kV, dedicated customer substation to be located approximately 1.25 miles west of Riverview Substation which will service 40MW of new load. Expansion of Riverview is needed to service the new CE substation. |  |  |  | 2021-07-02 | 2021-07-02 | 138 | 0 | Y | 6270000 | Bottom-Up
A in MTEP20 | B>A | East | METC | 18069 | Kalamazoo Load Transfer Interconnection | Construct a new four breaker ring bus. Cut in the METC Cork St.-Morrow 138kV circuit to feed the ring bus station. Connect two transformers, owned by Consumers Energy, to the new ring bus station. | MI | MI | Consumers Energy has provided notification to transfer load from the METC Morrow substation to a new Consumers Energy substation. The new switching station is needed to service the Consumers Energy load transfer from the METC Morrow substation. |  |  |  | 2022-10-01 | 2022-10-01 | 138 | 0 | Y |  | Bottom-Up
A in MTEP20 | B>A | East | METC | 18072 | Hubbard Lake – Spruce Road 138 kV Sag Remediation | The proposed solution is to completely remediate the sag on the Hubbard Lake – Spruce Road section of the Alpena – Iosco 138kV line. | MI | MI | The Hubbard Lake – Spruce Road section of the Alpena – Iosco 138kV circuit is projected to overload for the loss of the Keystone – Ludington #1 345 kV line and the loss of the Livingston – Gallagher – Tittabawassee 345 kV line. |  |  |  | 2023-12-31 | 2023-12-31 | 138 | 0 | Y |  | Bottom-Up
A in MTEP20 | B>A | East | METC | 18073 | Argenta - Riverview 138kV Rebuild | The proposed solution is to rebuild approximately 3 miles of the Argenta - Riverview 138kV circuit using 1431 ACSR conductor with double circuit steel structures. | MI | MI | The Argenta - Riverview 138kV circuit is projected to overload for shutdown plus contingency scenario, the worst involving the Argenta - Morrow 138kV line and Argenta - Battle Creek 345kV line. The identified overloaded equipment on this circuit is the conductor on the Argenta - Riverview circuit. The thermal violations are found on peak condition. |  |  |  | 2024-06-01 | 2024-06-01 | 138 | 0 | Y |  | Bottom-Up
A in MTEP20 | B>A | East | METC | 18084 | Moore Road - Coldwater 138kV Sag Remediation | The proposed solution is to remediate sag limit on the Moore Road - Coldwater 138kV section to increase its summer emergency rating to a minimum of 166 MVA (693 Amps). | MI | MI | The Moore Road - Coldwater 138kV circuit is projected to overload for shutdown plus contingency scenario, the worst involving the Batavia - Coldwater and Newton - Wagner 138kV lines. The identified overloaded equipment on this circuit is the sag on the Moore Road - Coldwater circuit. The thermal violations are found on off peak and off-peak conditions. |  |  |  | 2023-12-31 | 2023-12-31 | 138 | 0 | Y |  | Bottom-Up
A in MTEP20 | B>A | East | METC | 18112 | Kenowa 345 kV Breaker Installation | Complete row 33 of the Kenowa substation by adding 3 breakers and associated equipment. This addition creates a breaker-and-a-half scheme at Kenowa. | MI | MI | Completing row 33 with standard breakers converts Kenowa into a breaker-and-a-half scheme, which increases system reliability. It limits the amount of system split, apart from N-1-1 and outage + fault scenarios, reduces operational challenges, and assists relay protection efforts. |  |  |  | 2022-12-31 | 2022-12-31 | 345 | 0 | Y |  | Bottom-Up
A in MTEP20 | B>A | East | METC | 18133 | Pere Marquette 138 kV 5M9 & 7W8 Station Eq. Upgrades | Upgrade two breakers (at positions 5M9 and 7W8) and other terminal station equipment at the Pere Marquette 138 kV station. | MI | MI | Station equipment at Pere Marquette 138 kV is projected to overload for various scenarios, the worst involving the loss of the Keystone – Ludington 345 kV line and the Pere Marquette – Michigan Power 138 kV line. The identified overloaded equipment is the transformer #2 bus, and the breakers, switches and buses at positions 5M9 and 7W8. The thermal violations are found on multiple cases. |  |  |  | 2022-12-31 | 2022-12-31 | 138 | 0 | Y |  | Bottom-Up
A in MTEP20 | B>A | East | METC | 18147 | Bard Road – Clare Juction – Warren 138 kV Rebuild | Rebuild 16.4 miles of the Bard Road – Clare Junction section of the Bard Road – Warren 138kV circuit and to rebuild 3.3 miles of the Clare Junction – Warren section of the Bard Road – Warren 138kV circuit with 954 ACSR utilizing future 230 kV double circuit construction initially operated as 138 kV single circuit with adjacent side left vacant for future use. | MI | MI | The Clare Junction – Warren section of the Bard Road – Warren 138kV circuit is projected to overload for the loss of the Keystone – Ludington #1 345 kV line and the loss of the Livingston – Gallagher – Tittabawassee 345 kV line. The identified overload on this circuit is the conductor. The thermal violations are only found on 85% peak cases. The Bard Road – Clare Junction section of the Bard Road – Warren 138kV circuit is projected to marginally overload for the loss of the Keystone – Ludington #1 345 kV line and the loss of the Livingston – Gallagher – Tittabawassee 345 kV line. The identified overload on this circuit is the conductor. The thermal violations are only found on 85% peak cases. |  |  |  | 2024-06-01 | 2024-06-01 | 138 | 0 | Y |  | Bottom-Up
A in MTEP20 | B>A | East | METC | 18164 | Amber - Pere Marquette #2 138 kV | Construct a new line from Amber to Pere Marquette utilizing existing rights of way. Rebuild 0.62 miles from Amber to the Pere Marquette – Stronach 138 kV line with 954 ACSR utilizing future 230 kV double circuit construction initially operated as 138 kV single circuit with adjacent side left vacant for future use. Rebuild 0.72 miles of the existing single circuit Pere Marquette – Stronach 138 kV line with double circuit 138 kV construction and install 954 ACSR conductor on one side for the new Amber – Pere Marquette #2 138 kV line and 795 ACSS conductor on the other side for the existing Pere Marquette – Stronach 138 kV line. | MI | MI | The Amber – Pere Marquette #1 138 kV line is projected to become overloaded for numerous contingency types with the most sever loadings caused by shutdown plus contingencies involving either the Pere Marquette – Stronach 138 kV or Pere Marquette – Lake County 138 kV lines plus another transmission facility. The overloads were identified in the 2021, 2024, and 2029 peak load models with the Ludington units generating regardless of the directional flow across the Michigan-Ontario interface. |  |  |  | 2024-06-01 | 2024-06-01 | 138 | 0 | Y |  | Bottom-Up
A in MTEP20 | B>A | East | METC | 18187 | Pere Marquette – Stronach 138 kV Sag Remediation | Completely remediate the sag on the Pere Marquette – Stronach 138 kV line and replace terminal equipment at the Stronach end of the line. | MI | MI | The Pere Marquette – Stronach 138 kV circuit is projected to overload for the loss of the Keystone – Ludington #1 345 kV line and the loss of the Livingston – Gallagher – Tittabawassee 345 kV line. The identified overload on this circuit is the sag limit for the conductor. The thermal violations found in 85% peak conditions. |  |  |  | 2023-12-31 | 2023-12-31 | 138 | 0 | Y |  | Bottom-Up
A in MTEP20 | B>A | East | METC | 18190 | Dort 138 kV Station Rebuild | Rebuild Dort 138 kV station with a new control house at a new site approximately 0.5 miles to the south utilizing new equipment in a four-row, breaker-and-a-half scheme configuration. The new 138 kV station to be built will be called Mott Lake. This new 138 kV station would reduce equipment failures, unplanned outages, and repair costs. In addition, it would enable routine maintenance to be performed again in a safe and efficient manner. | MI | MI | The Dort 138 kV station is an early-1950’s legacy station that was acquired from Consumers Energy as part of the METC acquisition. Much of the equipment has been in-service for several decades and has been identified as being in poor condition, a source of failure, and a safety hazard by the Asset Management Department at ITC. Furthermore, the configuration of the station also makes it difficult to perform routine maintenance on equipment. Some specific examples of the concerns are as follows: • Based on the oldest material requisition, the infrastructure at the station dates back to 1950. The oldest oil circuit breakers are from 1967 vintage and it’s assumed that the switches, insulators, and strain bus are approximately the same age. • There are known issues with aged, failing insulators. Visual inspections confirm that hundreds of old cap and pin insulators used in horizontal and strain configurations are cracked. Several have been blown by the wind and broke. • Based off field verification, there are multiple bent bus supports that are compromising their structural integrity. Additionally, there are many locations where the ground grid has started to become exposed. • The disconnects that have been accessible enough to replace have required bus modifications that put stress and on the switch pads that make them prone to early failure. • Some key detractors to routine bus inspections are the sequencing of shutdowns (two lines at a time) and hanging personal grounds in tight clearances. o There is a 50 ft. working height associated with the bus work and limited space exists to set up equipment. The 8 ft. clearance between the Blue and White buses is an inadequate amount of space for crane or personnel to work in. o Bus is Copper Tube bus that has known issues with having bus splice stress crack failures. • Spare parts for 37 of the 42 older bus disconnects are unavailable or supported by the manufacturer. • There are clearance issues when sparing/bypassing a breaker to inspect it since the bypass disconnects are located just above the bushings. • Small ‘dog houses’ type relay control houses limit the safe working area for technicians. The condition of the control houses lack climate control for the sensitive relaying, are prone to rodent intrusion. Relay houses have asbestos inside them. • There are crumbling foundations and woodchucks burrowing under some of the cement foundations. • There are relay thermal loadability issues on the 500 position. In addition to the issues primary equipment issues documented above there are several protection and control related issues including having small control buildings that have maintenance, safety, and human performance concerns due to the buildings’ age and space constraints. Most of METC’s relaying and controls require high operations and maintenance expenses due to their age. The protection panels being dispersed into many small control buildings creates human performance issues with small workspace and difficult lighting. Additionally, lack of available panel space creates difficulty replacing relaying without extended shutdowns. |  |  |  | 2024-06-01 | 2024-06-01 | 138 | 0 | Y |  | Bottom-Up
A in MTEP20 | B>A | East | METC | 18238 | Morrow (JK Ave) 138 kV Station Rebuild | Rebuild Morrow 138 kV station at a new site approximately 1.35 miles to the north utilizing new equipment in a five-row, breaker-and-a-half scheme configuration. The new 138 kV station to be built will be called JK Ave. Acquire new property as necessary and install (15) 138 kV, 3000 A breakers with at least 40 kA interrupting capability in a five-row, breaker-and-a-half scheme configuration for this new station. Redirect all circuits currently at the Morrow 138 kV station into the new JK Ave 138 kV station and connect CE’s step-down transformers (TB) #1 and #2, and Kalamazoo River Generation Station via radial feeds into the new station. | MI | MI | The Morrow 138 kV station is an early-1950’s vintage station. The station high voltage electrical equipment has been in-service for several decades and has realized the end of its useful life. This equipment is dated (requires the use of operating practices that do not employ the safety measure designed in modern equipment), a source of failure, emergency maintenance, and in need of a wholesale replacement. The station was designed in accordance with design practices of the era. ITC and the industry’s design practices today - utilizing modern high voltage electrical equipment - produces a reliable, safe, accessible, and operationally flexible station. As it stands today, Morrow station’s design and integrity makes it difficult to perform routine maintenance on equipment and presents challenges when conducting routine operations. Furthermore the present station design is such that a single faulted breaker will deenergize the entire station, dropping network load from 7 lines, 1 generation, and 3 sub-transmission transformers. |  |  |  | 2024-12-31 | 2024-12-31 | 138 | 0 | Y |  | Bottom-Up
A in MTEP20 | B>A | East | METC | 18239 | 2023 METC Asset Replacement Program | Replace aging and outdated equipment at a pace that will insure each type of equipment is replaced near its projected end of life. | MI | MI | Replace aging and outdated equipment on a cycle that will ensure each piece of equipment is replaced near its expected end of life. Modern equipment can improve reliability, use state of the art technology, and typically will allow for longer maintenance intervals. New equipment is also commonly equipped with better monitoring and alarming functionality giving improved remote supervision. All of this will help to reduce overall maintenance costs. The Asset Replacement program includes a variety of replacement programs for several types of equipment including but not limited to: • Circuit Breakers/switchers • Protective equipment (relays/control) • DC battery and charging systems • Surge Arresters • Instrument Transformers • Disconnect Switches • Wood poles • Miscellaneous line equipment (insulators, cross-arms, etc.) |  |  |  | 2023-12-31 | 2023-12-31 | 345 | 138 | Y | 25690750 | Bottom-Up
A in MTEP20 | B>A | East | METC | 18243 | Battle Creek Transformer 2 Replacement | Replace Battle Creek 345/138kV transformer #2 with a new transformer. | MI | MI | The transformer has reached the end of it's life. A detailed project justification document will be uploaded as soon as it's available. |  |  |  | 2023-12-31 | 2023-12-31 | 345 | 138 | Y | 5282500 | Bottom-Up
A in MTEP20 | B>A | East | METC | 18244 | Gallagher Transformer #2 Replacement | Replace Gallagher 345/138kV Transformer #2 with a new transformer | MI | MI | The transformer has reached the end of its life. A detailed project justification document will be uploaded as soon as it's available. |  |  |  | 2023-12-31 | 2023-12-31 | 345 | 138 | Y | 5282500 | Bottom-Up
A in MTEP20 | B>A | East | METC | 18245 | Kenowa 345kV Reactor 33F Replacement | Replace Kenowa 345kV Shunt Reactor #33F with a new reactor. | MI | MI | The reactor has reached the end of its life. A detailed project justification document will be uploaded as soon as it's available. |  |  |  | 2023-12-31 | 2023-12-31 | 345 | 0 | Y | 3445720 | Bottom-Up
A in MTEP20 | B>A | West | MPPA | 18003 | Barlow to Parsons Line Rebuild | Rebuild 2.73 miles of 69kV line between Barlow and Parsons. Replace 2.73 miles of #477 ACSR with .58 miles of twin #1000 MCM copper under airport flight path and 1.42 miles of #795 ACSS. Rebuild requires Switching Station upgrades at Barlow Substation. | MI | MI | MISO has identified this line as a limiting element in two contingencies |  |  |  | 2020-12-31 | 2022-11-01 | 69 | 69 | Y | 4000000 | Bottom-Up
A in MTEP20 | B>A | East | WPSC | 14004 | Hagensville Interconnection Line | Construct approximately 0.25 miles of new 138kV transmission line to connect the Grand Lake Distribution Station to METC’s 138 kV Port Calcite to Rockport transmission line. | MI | MI | New Construction |  |  |  | 2022-12-31 | 2022-12-31 | 138 | 0 | Y | 260000 | Bottom-Up
A in MTEP20 | B>A | East | WPSC | 14005 | Hammond Bay Interconnection Line | Construct approximately 2 miles of new transmission line to connect the Hammond Bay Distribution Station to METC’s 138 kV transmission line. | MI | MI | New Construction |  |  |  | 2022-12-31 | 2022-12-31 | 138 | 0 | Y | 900000 | Bottom-Up
A in MTEP20 | B>A | East | WPSC | 17204 | Vestaburg Transformer Upgrade | Wolverine to install transformer with increased capacity at the Vestaburg Transmission station in order to support the J589 generation interconnection. The capacity of the new transformer will be 168MVA. | MI | MI | Upgrades needed to connect MISO generator J589 to METC 138kV system |  |  |  | 2019-12-31 | 2019-12-31 | 138 | 0 | Y | 3520000 | Bottom-Up
A in MTEP20 | B>A | East | WPSC | 18011 | Atlanta to Airport 138kV Rebuild | Rebuild and upgrade 31.5 miles of 138 kV with double circuit steel poles, 795ACSS conductor, and OPGW. | MI | MI | Age and Condition based. |  |  |  | 2023-12-31 | 2023-12-31 | 138 | 0 | Y | 15500000 | Bottom-Up
A in MTEP20 | B>A | East | WPSC | 18015 | Cadillac Substation Line Modifications | Line modifications including structure relocation and switch replacement in order to accommodate a new Cadillac distribution station. | MI | MI | Distribution interconnection. |  |  |  | 2021-12-31 | 2021-12-31 | 69 | 0 | Y | 1000000 | Bottom-Up
A in MTEP20 | B>A | East | WPSC | 18021 | Eastport 69kV BUS replacement | Rebuild the existing 69kV bus to accommodate facility equipment replacement. | MI | MI | Needed for aging infrastructure. |  |  |  | 2021-12-31 | 2021-12-31 | 69 | 0 | Y | 170000 | Bottom-Up
A in MTEP20 | B>A | East | WPSC | 18022 | Westwood 69kV BUS replacement | Rebuild the existing 69kV bus to accommodate facility equipment replacement. | MI | MI | Needed for aging infrastructure. |  |  |  | 2022-12-31 | 2022-12-31 | 69 | 0 | Y | 170000 | Bottom-Up
A in MTEP20 | B>A | East | WPSC | 18023 | Eaton Rapids 69kV BUS replacement | Rebuild the existing 69kV bus to accommodate facility equipment replacement. | MI | MI | Needed for aging infastructure. |  |  |  | 2022-12-31 | 2022-12-31 | 69 | 0 | Y | 170000 | Bottom-Up
A in MTEP20 | B>A | East | WPSC | 18024 | Atlanta 69kV BUS replacement | Rebuild the existing 69kV bus to accommodate station equipment replacement. | MI | MI | Needed for aging infrastructure. |  |  |  | 2022-12-31 | 2022-12-31 | 69 | 0 | Y | 170000 | Bottom-Up
A in MTEP20 | B>A | East | WPSC | 18026 | Hawks 69kV BUS replacement | Rebuild the existing 69kV bus to accommodate equipment replacement at station. | MI | MI | Needed for aging infrastructure. |  |  |  | 2022-12-31 | 2022-12-31 | 69 | 0 | Y | 170000 | Bottom-Up
A in MTEP20 | B>A | East | WPSC | 18027 | Hammond Bay 138kV BUS replacement | 138kV BUS replacement in order to accommodate voltage increase. | MI | MI | Aging infrastructure. |  |  |  | 2021-12-31 | 2021-12-31 | 138 | 0 | Y | 170000 | Bottom-Up
A in MTEP20 | B>A | East | WPSC | 18028 | Hagensville 138kV BUS replacement | Install BUS to 138kV standard to accommodate voltage conversion. | MI | MI | Aging infrastructure. |  |  |  | 2021-12-31 | 2021-12-31 | 138 | 0 | Y | 170000 | Bottom-Up
A in MTEP19 | B>A | West | ATC | 7586 | Atlantic SS, 138/69 kV Transformer Replacement and Bus Reconfiguation | - Deenergize and remove the existing Atlantic 138/69 kV transformer - Install a new 138/69 kV transformer - Reconfigure the Atlantic substations 138 kV and 69 kV bus work | MI | MI | Non BES - Reliability | Other | Not Shared | Reliability | 2022-12-31 | 2022-12-31 | 138 | 69 | Y | 6600000 | Bottom-Up
A in MTEP19 | B>A | West | ATC | 15345 | Presque Isle - Tilden 138kV, loop and uprate | -Reconfigure the existing Presque Isle - Tilden 138kV line to loop into the existing National substation -Uprate the National - Tilden portion of the 138kV line -National SS control house, relay and circuit breaker replacements driven by asset renewal | MI | MI | Reliability | BRP |  |  | 2022-12-31 | 2022-12-31 | 138 | 0 | Y | 12000000 | Bottom-Up
A in MTEP19 | B>A | West | ATC | 15933 | NLKG31 Tap - Greenstone SS 138 kV new T-line | ATC to create new 138kV tap on NLKG31 and construct 2.2 miles of 138kV single circuit to UMERC’s Greenstone substation. | MI | MI | Reliability - Operational Flexibility | Other |  | Reliability | 2022-06-01 | 2022-06-01 | 138 | 138 | Y | 5200000 | Bottom-Up
A in MTEP19 | B>A | West | ATC | 16492 | J849, Chandler SS, Interconnection Facilities and Network Upgrades | J849 Interconnection request is for a new 125 MW solar farm to be connected to the open 138 kV bus position at Chandler. | MI | MI | GIP | GIP |  |  | 2022-01-07 | 2022-01-27 | 138 | 0 | Y | 3036785 | Externally Driven
A in MTEP19 | B>A | West | ATC | 17064 | J928/J849 Indian Lake Common Use Upgrades | The ground grid upgrades at Indian Lake SS are split between the J928 and J849 interconnections. 91% will be charged to J928 and 9% will be charged to J849. All ground gird improvements must be completed prior to the initial 20 MW coming online which is 10-15-2019. | MI | MI | GIP | GIP | Shared |  | 2019-10-13 | 2019-10-13 | 138 | 69 | Y | 173012 | Externally Driven
A in MTEP19 | B>A | East | CETO | 15717 | CE Substation Equipment Replacement Program - 2021 | Replace damaged or defective substation equipment, not including breakers, with new equipment | MI | MI | Replace substation equipment that is defective, damaged, or fails testing parameters to improve system reliability and address safety concerns | Other |  | Reliability | 2021-12-31 | 2021-12-31 | 138 | 0 | Y | 840000 | Bottom-Up
A in MTEP19 | B>A | East | CETO | 15718 | CE Pole & Line Equipment Replacement Program - 2021 | Replace damaged or defective poles, towers, cross arms, insulators, guying, and switches, as needed, to maintain the lines' condition | MI | MI | Replace structures and line equipment that are defective or damaged to maintain line performance, reduce outages, address code clearance, and/or address safety concerns | Other |  | Age and Condition | 2021-12-31 | 2021-12-31 | 138 | 0 | Y | 570000 | Bottom-Up
A in MTEP19 | B>A | East | CETO | 15720 | Muskegon Heights #1 Line Rebuild | Rebuild a portion of the Muskegon Heights #1 138 kV Line, approximately 1.8 miles, utilizing 138 kV single circuit construction | MI | MI | This portion of the line is constructed with towers installed in 1928. Experience with these vintage of towers has shown significant ground level rusting which will lead to tower failure and line outages. | Other |  | Age and Condition | 2021-06-01 | 2021-06-01 | 138 | 0 | Y | 790000 | Bottom-Up
A in MTEP19 | B>A | East | CETO | 15721 | Verona-Elm Street Line Rebuild | Rebuild the Verona-Elm Street 138 kV Line, approximately 2.2 miles, utilizing 138 kV double circuit construction and 336.4 ACSR conductor | MI | MI | This portion of the line is constructed with towers installed in 1920. Experience with these vintage of towers has shown significant ground level rusting which will lead to tower failure and line outages. | Other |  | Age and Condition | 2021-12-31 | 2021-12-31 | 138 | 0 | Y | 1000000 | Bottom-Up
A in MTEP19 | B>A | East | CETO | 15722 | Saginaw River-Shale Line | Construct a new 138 kV line from Saginaw River Substation to the new Shale Substation | MI | MI | METC has identified a plan to install a new station named Shale, MISO MTEP#14824. METC's plan will require Consumers Energy to reconnect its Saginaw River Substation to the new station with a new transmission line. | Other |  | Other Local Needs | 2022-12-31 | 2022-12-31 | 138 | 0 | Y | 200000 | Bottom-Up
A in MTEP19 | B>A | East | CETO | 16044 | Cobb Rebuild - CETO 138 kV Lines | Construct new 138 kV lines from the existing Cobb & Muskegon Heights Substations to METC's rebuilt Cobb Station | MI | MI | METC has identified a plan to rebuild Cobb Station, MISO MTEP#15942. METC's plan will require Consumers Energy to reconnect its Cobb and Muskegon Heights Substations to the new station with new transmission lines as dictated by METC's project scope. | Other |  | Other Local Needs | 2023-12-31 | 2023-12-31 | 138 | 0 | Y | 800000 | Bottom-Up
A in MTEP19 | B>A | East | ITCT | 12003 | Milan - Pioneer 120 kV Rebuild | Rebuild a ~4.0 mile-long portion of the Milan – Pioneer 120 kV line that is comprised of 477 ACSR conductor only by replacing the existing assets (all structures and 477 ACSR conductor) with new 120 kV double-circuit structures that are designed for 954 ACSR conductor, installing this new conductor along with OPGW for the Milan – Pioneer 120 kV line only, and reattaching the existing 477 ACSR conductor of the Noble – Superior 120 kV line to the other side of the new structures. | MI | MI | The Milan – Pioneer 120 kV line is projected to become overloaded for the Superior 120 kV Position HJ breaker failure contingency. The overloads were identified in the 2021 near-term and 2026 long-term peak load models with flow to and from ITCT across the Michigan-Ontario interface. The Milan - Pioneer 120 kV circuit is projected to marginally overload for a breaker failure at Superior 120 kV and several shutdown-plus-contingency that trip DTE’s transformer #101 and or #102 at that station. The limiting elements on this circuit are the 477 ACSR conductor and sag limit. | BRP |  |  | 2023-12-31 | 2023-12-31 | 120 | 0 | Y | 6000000 | Bottom-Up
A in MTEP19 | B>A | East | ITCT | 13816 | Pioneer – Superior 120 kV Rebuild | Rebuild approximately 3.16 miles of 477 ACSR to 954 ACSR from Pioneer to McAuley to Superior on double-circuit, 120 kV towers. Upgrade station equipment at Superior to 954 ACSR. Also, 3.16 miles of 477 ACSR conductor of the Noble to Superior 120 kV line that shares common structure with Pioneer – Superior 120 kV will be upgraded to 954 ACSR. Install OPGW on the rebuilt section. | MI | MI | The Pioneer – McAuley – Superior 120 kV circuit is projected to overload in the 5 and 10 year cases. The thermal violation occurs in different contingencies with most of them involving the loss of Milan 345/120 kV transformer or Milan – Pioneer 120 kV line. | BRP |  |  | 2023-12-31 | 2023-12-31 | 120 | 0 | Y | 4940000 | Bottom-Up
A in MTEP19 | B>A | East | ITCT | 14924 | Morton Interconnection | Morton is a new 120kV interconnection. Station will be a straight bus with a section breaker and two line breakers. Morton will be fed by cutting in the Douglass - Visteon 120kV line. | MI | MI | Interconnection is needed to serve 5.75 MW of new load, and to support the relocation of 27.55 MW of load from DTE stations. | Other |  | Load Growth | 2021-12-31 | 2021-12-31 | 120 | 0 | Y | 3540000 | Bottom-Up
A in MTEP19 | B>A | East | ITCT | 15704 | Gramer Interconnection | Gramer 120kV is a straight bus station with 1 section breaker and 2 line breakers. This will require 2 miles of new 120kV DCT to loop in the Jewel - St.Clair #2 120kV line for transmission service. DTE will have 2 120/40kV transformer which will be networked with DTE's existing 40kV system. | MI | MI | DTE interconnection request. DTE needs an additional 120kV line to solve local problems on its 40kV system. | Other |  | Load Growth | 2021-03-31 | 2021-03-31 | 120 | 0 | Y | 10245000 | Bottom-Up
A in MTEP19 | B>A | East | ITCT | 15739 | Northeast 120 kV Breaker HE Replacement | Replace the existing Northeast 120 kV circuit breaker HE with a circuit breaker capable of interrupting at least 50 kA. | MI | MI | The 2018 ITC short circuit analysis demonstrates that the Northeast 120 kV circuit breaker HE is at risk of having to interrupt faults as high as 98.2%of its capability. | BRP |  |  | 2020-12-31 | 2020-12-31 | 120 | 0 | Y | 254000 | Bottom-Up
A in MTEP19 | B>A | East | ITCT | 15741 | Quaker 230kV Breaker Installation Project | Install a 230kV breaker on the high side of T251 at Quaker for the Quaker – Wixom line. The new breaker would have a dedicated breaker control relay. | MI | MI | The Quaker T251 currently is a line terminated transformer on the Quaker – Wixom line. The protection of this transformer relies on sending transfer trip to the remote terminal (Wixom). The installation of a 230kV breaker will increase reliability by performing local tripping, which improves system protection. • Adds local tripping for the Quaker 230/120 kV Transformer #251 resulting in: ¿ 25% faster fault clearing. ¿ Increased reliability of transformer protection as primary fault clearing does not rely on power line carrier scheme to trip the remote end breakers. • Less sensitive protection settings by eliminating in line transformer, resulting in: ¿ Faster backup clearing times without risk of miscoordination. ¿ Eliminate risk of overtrip caused by transformer inrush. • Install redundant ITC standard protection design, resulting in the following benefits: ¿ Redundant high-speed line protection with modern microprocessor line relays and power line carrier units. ¿ Redundant transfer trip for breaker failure. | Other |  | Reliability | 2021-12-31 | 2021-12-31 | 120 | 0 | Y | 508000 | Bottom-Up
A in MTEP19 | B>A | East | ITCT | 15768 | Corktown | ITCT will construct a new 4 breaker ring bus 120kV substation, named Corktown. ITCT will loop the St. Antoine - Waterman 120kV circuit into the new station. | MI | MI | This is a DTE load interconnection request to serve 10 MW of new load and 24MW of relocated load from DTE’s Kent and Gibson Substations. | Other |  | Load Growth | 2022-03-31 | 2022-03-31 | 120 | 0 | Y | 28876000 | Bottom-Up
A in MTEP19 | B>A | East | ITCT | 15776 | Juliet | ITCT will construct a new straight bus 120kV substation tentatively named Juliet. ITCT will loop in the Adams – Fitz 120kV circuit into the new substation. ITCT will install OPGW between Adams and new substation. | MI | MI | This is a DTE load interconnection request. The new station will serve 20.6MVA of relocated load from DTE’s Adams Substation. | Other |  | Load Growth | 2020-12-31 | 2020-12-31 | 120 | 0 | Y | 4165000 | Bottom-Up
A in MTEP19 | B>A | East | ITCT | 15783 | Croswell | ITCT will install a new 120 kV breaker with associated disconnects at the Lee substation. ITCT will construct approximately 7.5 miles of a new 120 kV circuit between Lee and the new substation in Croswell. | MI | MI | The City of Croswell has requested a new 120kV load interconnection to serve 11 MVA of relocated load from DTE’s 41.6 kV sub-transmission system. | Other |  | Load Growth | 2021-12-31 | 2021-12-31 | 120 | 0 | Y | 8659000 | Bottom-Up
A in MTEP19 | B>A | East | ITCT | 15862 | Adams – Burns 2 120 kV Rebuild | Rebuild approximately 0.3 mile of 795 ACSR conductor to 1431 ACSR to match the rest of the conductor on this Adams – Burns 2 120 kV branch. | MI | MI | The 120 kV section between Adams and Burns 2 tap is projected to overload for various contingencies, including T-1, for the 2, 5, and 10 year cases in the 2018 assessment. The overloaded facility is the 795 ACSR conductor and the sag limit on this section. | BRP |  |  | 2024-06-01 | 2024-06-01 | 120 | 0 | Y | 1130000 | Bottom-Up
A in MTEP19 | B>A | East | ITCT | 15863 | Arizona – Dayton 120 kV Rebuild | Rebuild approximately 2.7 miles of 120 kV line from Arizona to Dayton using 954 ACSR conductor. Also upgrade station equipment at Arizona. | MI | MI | Dayton is the interconnection point that delivers Wolverine’s generation from Judd to the 120 kV transmission network. This station has three 120 kV outlets: one goes toward Brownstown 120 kV (through Alamo), another goes toward Superior 120 kV (through Collins), and the third path goes toward Superior 120 kV and Wayne 120 kV (through Arizona, Scottsdale, Willow Run, and Zebra). The Arizona – Dayton 120 kV circuit is projected to overload for shutdown-plus-contingency and double-circuit tower outage that take out the other two paths. | BRP |  |  | 2022-12-31 | 2022-12-31 | 120 | 0 | Y | 7000000 | Bottom-Up
A in MTEP19 | B>A | East | ITCT | 15864 | Arizona – Scottsdale 120 kV Rebuild | Rebuild approximately 1.0 mile of 120 kV line from Arizona to Scottsdale using 954 ACSR conductor and upgrade station equipment at both ends. | MI | MI | Dayton is the interconnection point that delivers Wolverine’s generation from Judd to the 120 kV transmission network. This station has three 120 kV outlets: one goes toward Brownstown 120 kV (through Alamo), another goes toward Superior 120 kV (through Collins), and the third path goes toward Superior 120 kV and Wayne 120 kV (through Arizona, Scottsdale, Willow Run, and Zebra). The Arizona – Scottsdale 120 kV circuit is projected to overload for shutdown-plus-contingency and double-circuit tower outage that take out the other two paths. | BRP |  |  | 2022-12-31 | 2022-12-31 | 120 | 0 | Y | 2692000 | Bottom-Up
A in MTEP19 | B>A | East | ITCT | 15865 | Navarre – A-I-N – Ironton 120 kV Rebuild | Rebuild approximately 7.7 miles from Navarre to Adelaide-Ironton-Navarre junction to Ironton with 1431 ACSR conductor. Also upgrade station equipment at both ends. | MI | MI | The Navarre – Adelaide-Ironton-Navarre 120 kV and Adelaide-Ironton-Navarre – Ironton 120 kV sections are projected to overload for many T-2 contingencies in the 5 and 10 year cases. Most of the T-2 contingencies that cause this thermal violation involve the loss of Navarre – River Rouge 120 kV circuit. When the Navarre – River Rouge 120 kV circuit is out, the Navarre – Adelaide – Ironton 120 kV line carries extra weight to deliver power from Navarre into the River Rouge region (through Ironton). Taking another feed that supplies power to this River Rouge area will cause the Navarre – Adelaide – Ironton 120 kV circuit to overload its thermal limit. | BRP |  |  | 2024-06-01 | 2024-06-01 | 120 | 0 | Y | 18228000 | Bottom-Up
A in MTEP19 | B>A | East | ITCT | 15866 | Newburgh – Peru 120 kV Rebuild | Rebuild approximately 2.2 miles of 477 ACSR conductor to 1431 ACSR on the Newburgh – Sport 2 120 kV section to match with the rest of the circuit. | MI | MI | The 120 kV section from Newburgh to Sport 2 tap of the Newburgh – Peru 120 kV circuit is projected to be overloaded for a double-circuit tower and multiple T-2 contingencies in the 2018 assessment. The overloaded facility is the 477 ACSR conductor section of this circuit. | BRP |  |  | 2023-12-31 | 2023-12-31 | 120 | 0 | Y | 4520000 | Bottom-Up
A in MTEP19 | B>A | East | ITCT | 15868 | Brock - Elm 120 kV Rebuild | Rebuild the 795 ACSR section (approximately 1.0 mile) on Brock – Elm 120 kV circuit to 1431 ACSR. Also upgrade station equipment at Elm 120 kV. | MI | MI | The Brock to Elm 120 kV circuit is projected to overload for shutdown-plus-contingency that takes out the two feeds from Wayne to Newburgh. The limiting elements on this circuit are the 795 ACSR conductor and station equipment at Elm 120 kV. | BRP |  |  | 2023-12-31 | 2023-12-31 | 120 | 0 | Y | 3533000 | Bottom-Up
A in MTEP19 | B>A | East | ITCT | 15869 | Brownstown 120 kV - Upgrade GB Station Equipment | Upgrade the station equipment at Brownstown 120 kV position “GB”. | MI | MI | The 345/120kV transformer #301 at Brownstown projected to be marginally overloaded for a shutdown-plus-contingency that takes out Navarre 230/120kV transformer and Brownstown 345/120kV transformer #304. The limiting element on this transformer branch is the 120 kV station equipment at Brownstown position “GB”. | BRP |  |  | 2021-12-31 | 2021-12-31 | 120 | 0 | Y | 325000 | Bottom-Up
A in MTEP19 | B>A | East | ITCT | 15879 | Monroe - Lulu 345 kV Station Equipment Upgrade | Upgrade the station equipment at Monroe 345 kV positions “MF” and “MM”. | MI | MI | The Monroe – Lulu section of the Milan-Monroe-Morocco 345 kV circuit is projected to be overloaded for T-1 and other contingency types that involve the loss of Monroe – Lallendorf 345 kV circuit. The overloaded facilities are the station equipment at Monroe 345 kV positions “MF” and “MM”. | BRP |  |  | 2021-12-31 | 2021-12-31 | 345 | 0 | Y | 970000 | Bottom-Up
A in MTEP19 | B>A | East | ITCT | 15881 | Bismarck - Golf 120 kV Sag Remediation | Raise the sag limit on the Bismarck – Golf 120 kV line to at least 253 MVA. | MI | MI | The Bismarck – Golf 120 kV circuit is projected to be overloaded for several shutdown-plus-contingency that involve the loss of the Macomb – Stephens 120 kV line. The identified overloaded equipment on this circuit is the sag limit. | BRP |  |  | 2021-12-31 | 2021-12-31 | 120 | 0 | Y | 630000 | Bottom-Up
A in MTEP19 | B>A | East | ITCT | 15882 | Bismarck 120 kV – Upgrade JC Station Equipment | Upgrade the station equipment at Bismarck 120 kV position “JC”. | MI | MI | The 345/120kV transformer #301 at Bismarck projected to overload for a shutdown-plus-contingency that takes two 345/120kV transformers at Stphens. The limiting element on this transformer branch is station equipment at Bismarck 120 kV position “JC”. | BRP |  |  | 2021-12-31 | 2021-12-31 | 120 | 0 | Y | 34000 | Bottom-Up
A in MTEP19 | B>A | East | ITCT | 15884 | Bloomfield - Hood 120 kV Station Equipment Upgrade | Upgrade the station equipment at Bloomfield 120 kV position “HE”. | MI | MI | The Bloomfield – Bartlett (toward Hood) 120 kV circuit is projected to overload for a shutdown-plus-contingency and double-circuit tower that take out Pontiac – Placid 345 kV and Pontiac – Wixom 345 kV lines. The overloaded facility is the station equipment at Bloomfield 120 kV position “HE”. This thermal violation only occurs in the 5-year, 85%-peak IN case. | BRP |  |  | 2021-12-31 | 2021-12-31 | 120 | 0 | Y | 86000 | Bottom-Up
A in MTEP19 | B>A | East | ITCT | 15885 | Giddings - Colorado 120 kV Sag Remediation | Raise the sag limit on the Giddings – Colorado 120 kV section to at least 272 MVA. | MI | MI | The 120 kV section between Giddings 1 tap and Colorado 2 tap of the Bloomfield – Sunbird 120 kV circuit is projected to be overloaded for several shutdown-plus-contingency that involve the loss of the Pontiac - Joslyn 120 kV and or Pontiac – Walton 120 kV lines. The identified overloaded equipment on this circuit is the sag limit. | BRP |  |  | 2021-12-31 | 2021-12-31 | 120 | 0 | Y | 360000 | Bottom-Up
A in MTEP19 | B>A | East | ITCT | 15886 | Ottawa - Yost 120 kV Reconductor | Reconductor one span of 954 ACSR to 1431 ACSR at each end of the Ottawa – Yost 120 kV circuit and upgrade the equipment at both stations. | MI | MI | The Ottawa – Yost 120 kV circuit is projected to overload for a shutdown-plus-contingency that takes out Hager – Sunset 120 kV and Hines – Wayne 120 kV line. The limiting elements on this circuit are the 954 ACSR conductor and equipment at both Ottawa and Yost 120 kV stations. | BRP |  |  | 2021-12-31 | 2021-12-31 | 120 | 0 | Y | 500000 | Bottom-Up
A in MTEP19 | B>A | East | ITCT | 15887 | Durant 120 kV 33.3 MVAR Capacitor | Install a 33.3 MVAR capacitor at Durant 120 kV station. | MI | MI | The Durant buses are projected to experience low voltages for a shutdown-plus-contingency that takes out Genoa – Madrid 120 kV and Durant – Placid 120 kV lines. | BRP |  |  | 2022-12-31 | 2022-12-31 | 120 | 0 | Y | 1100000 | Bottom-Up
A in MTEP19 | B>A | East | ITCT | 15888 | Scottsdale - Willow Run 120 kV Rebuild | Rebuild approximately 0.4 mile of 120 kV line from Scottsdale to Willow Run using 954 ACSR conductor and upgrade station equipment at both ends. | MI | MI | Dayton is the interconnection point that delivers Wolverine’s generation from Judd to the 120 kV transmission network. This station has three 120 kV outlets: one goes toward Brownstown 120 kV (through Alamo), another goes toward Superior 120 kV (through Collins), and the third path goes toward Superior 120 kV and Wayne 120 kV (through Arizona, Scottsdale, Willow Run, and Zebra). The Scottsdale – Willow Run 120 kV circuit is projected to overload for shutdown-plus-contingency and double-circuit tower outage that take out the other two paths. | BRP |  |  | 2022-12-31 | 2022-12-31 | 120 | 0 | Y | 1850000 | Bottom-Up
A in MTEP19 | B>A | East | ITCT | 15891 | ITCT Customer interconnections - Year 2022 | Customer interconnection requests and retirements less than $1 million with in service date in year 2022. | MI | MI | Customer Requests are often in need of interconnection on an expedited basis. This blanket allows interconnection requests of smaller nature to be quickly studied and connected by ITC. | Other |  | Load Growth | 2022-12-31 | 2022-12-31 | 120 | 0 | Y | 2000000 | Bottom-Up
A in MTEP19 | B>A | East | ITCT | 15892 | Superior 120 kV – Upgrade HJ Station Equipment | Upgrade the station equipment at Wayne 120 kV position “HJ”. | MI | MI | The 120 kV bus-tie between bus 101 and 102 at Superior is projected to overload for a shutdown-plus-contingency event that takes out the 345/120 kV transformer #301 at Wayne and a fault happening on DTE’s transformer #2 at this same station. The limiting element on this 120 kV bus-tie branch is the station equipment at Wayne position “HJ”. | BRP |  |  | 2021-12-31 | 2021-12-31 | 120 | 0 | Y | 330000 | Bottom-Up
A in MTEP19 | B>A | East | ITCT | 15895 | Trenton Channel 120 kV – Upgrade JP Station Equipment | Upgrade the station equipment at Trenton Channel 120 kV position “JP”. | MI | MI | The 120 kV bus-tie between bus 11 and 13 at Trenton Channel is projected to overload for several shutdown-plus-contingency that involve the loss of Brownstown 345/120kV transformer #301 and or Navarre 230/120kV transformer #201. The limiting element on this 120 kV bus-tie branch is the station equipment at Trenton Channel position “JP”. | BRP |  |  | 2021-12-31 | 2021-12-31 | 120 | 0 | Y | 252000 | Bottom-Up
A in MTEP19 | B>A | East | ITCT | 15897 | Trenton Channel - Taurus 120 kV Station Equipment Upgrade | Upgrade the station equipment at Trenton Channel 120 kV position “JR”. | MI | MI | The Trenton Channel – Taurus 120 kV circuit is projected to overload for a shutdown-plus-contingency that takes out Brownstown – Zephyr 120 kV line and Navarre 230/120kV transformer. The overloaded facility is the station equipment at Trenton Channel 120 kV position “JR”. | BRP |  |  | 2021-12-31 | 2021-12-31 | 120 | 0 | Y | 45000 | Bottom-Up
A in MTEP19 | B>A | East | ITCT | 15898 | Wayne 120 kV – Upgrade GQ Station Equipment | Upgrade the station equipment at Wayne 120 kV position “GQ”. | MI | MI | The 345/120kV transformer #301 at Wayne projected to be marginally overloaded for shutdown-plus-contingency events that take out the other 345/120kV transformer #303. The limiting element on this transformer branch is the station equipment at Wayne 120 kV position “GQ”. | BRP |  |  | 2021-12-31 | 2021-12-31 | 120 | 0 | Y | 75000 | Bottom-Up
A in MTEP19 | B>A | East | ITCT | 15904 | Wayne - Newburgh #2 120 kV Station Equipment Upgrade | Upgrade the station equipment at Wayne 120 kV position “GP” and Newburgh 120 kV position “HQ”. | MI | MI | The Wayne-Koppernick-Newburgh 120 kV line is projected to be overloaded for T-1 and other contingency types that involve the loss of Wayne – Newburgh #1 120 kV circuit. The overloaded facilities are the equipment at Wayne and Newburgh 120 kV stations. | BRP |  |  | 2021-12-31 | 2021-12-31 | 120 | 0 | Y | 1000000 | Bottom-Up
A in MTEP19 | B>A | East | ITCT | 15905 | Willow Run - Zebra 120 kV Rebuild | Rebuild approximately 4.6 miles of 120 kV line from Willow Run to Zebra using 954 ACSR conductor and upgrade station equipment at both ends. | MI | MI | Dayton is the interconnection point that delivers Wolverine’s generation from Judd to the 120 kV transmission network. This station has three 120 kV outlets: one goes toward Brownstown 120 kV (through Alamo), another goes toward Superior 120 kV (through Collins), and the third path goes toward Superior 120 kV and Wayne 120 kV (through Arizona, Scottsdale, Willow Run, and Zebra). The Scottsdale – Willow Run 120 kV circuit is projected to overload for shutdown-plus-contingency and double-circuit tower outage that take out the other two paths. | BRP |  |  | 2022-12-31 | 2022-12-31 | 120 | 0 | Y | 6212000 | Bottom-Up
A in MTEP19 | B>A | East | ITCT | 15908 | Newburgh 120 kV 33.3 MVAR Capacitor | Install a 33.3 MVAR capacitor at Newburgh 120 kV on bus 101. | MI | MI | The Newburgh buses are projected to experience low voltages for a shutdown-plus-contingency that takes out both Wayne – Newburgh 120 kV lines. | BRP |  |  | 2022-12-31 | 2022-12-31 | 120 | 0 | Y | 850000 | Bottom-Up
A in MTEP19 | B>A | East | ITCT | 15956 | Northeast – Stephens 230 kV Sag Remediation | Raise the sag limit on the Northeast – Stephens 230 kV line to at least 686 MVA and upgrade station equipment at Northeast 120 kV position “HE”. | MI | MI | The Northeast – Stephens 230 kV circuit projected to overload for many shutdown-plus-contingency that involve the loss of Bismarck – Redrun 230 kV and or Caniff – Stephens 345 kV lines. The limiting element on this circuit are sag limit and equipment at Northeast 120 kV position “HE”. | BRP |  |  | 2022-12-31 | 2022-12-31 | 230 | 0 | Y | 403400 | Bottom-Up
A in MTEP19 | B>A | East | ITCT | 15976 | 2022 ITCT Asset Replacement Program | Replace aging and outdated equipment on a cycle that will ensure each piece of equipment is replaced near its expected end of life. Modern equipment can improve reliability, use state of the art technology, and typically will allow for longer maintenance intervals. New equipment is also commonly equipped with better monitoring and alarming functionality giving improved remote supervision. All of this will help to reduce overall maintenance costs. | MI | MI | Equipment that is past its expected design life, utilizes outdated functionality or whose failure rates and maintenance requirements have increased the potential for misoperations and higher maintenance costs associated with their ongoing use. | Other |  | Age and Condition | 2022-12-31 | 2022-12-31 | 345 | 120 | Y | 49000000 | Bottom-Up
A in MTEP19 | B>A | East | ITCT | 15981 | Detroit Cable Project | Construct two new 120kV stations named Promenade and Island View and approximately 7 miles of new underground cable from Alfred 120 kV to Island View 120kV, from new Island View 120kV to Promenade 120kV, and from Promenade 120kV to Mack 120 kV. | MI | MI | DTE submitted interconnection requests to ITCT to interconnect two new loads (Promenade & Island View) in the Northeast Detroit area. Some of this load is added to the Mack/Essex load pocket area. As the system exist today, there is little margin for load growth in the area before circuits become overloaded for N-1-1 conditions. | Other |  | Load Growth | 2023-06-01 | 2023-06-01 | 120 | 0 | Y | 139500000 | Bottom-Up
A in MTEP19 | B>A | East | ITCT | 16004 | ITCT Pole Top Switch Additions/Replacement Program 2021 | Installing, or replacing as appropriate, pole-top switches at tap points of circuits will provide the operational flexibility to sectionalize parts of the line to isolate faults or perform maintenance work on it without having to shut down the entire circuit. | MI | MI | Without pole top switches in place, planned or unplanned outages to a transmission line will cause long outages to customers. | Other |  | Reliability | 2021-12-31 | 2021-12-31 | 120 | 0 | Y | 2400000 | Bottom-Up
A in MTEP19 | B>A | East | ITCT | 16006 | St. Clair - Stephens #2 345 kV Sag Remediation and Station Equipment Upgrade | The proposed solution is to completely remove sag limit on the St. Clair – Stephens #2 345kV to conductor limit and replace station equipment at Stephens and St. Clair substations. | MI | MI | The St. Clair – Stephens #2 345kV circuit is projected to overload for various shutdown plus contingency scenarios, the worst involving the Belle River – St. Clair and Jewell – St. Clair 345kV lines. The identified overloaded equipment on this circuit is the sag limit and station equipment at St. Clair and Stephen substations. The thermal violations are found on peak and off peak cases. | BRP |  |  | 2021-12-31 | 2021-12-31 | 345 | 0 | Y | 3550000 | Bottom-Up
A in MTEP19 | B>A | East | ITCT | 16008 | Pontiac – Placid 345 kV Sag Remediation | Remediate the sag limit on the Pontiac - Placid 345 kV line to 1543 MVA (2582 Amps) for summer emergency rating. Also, upgrade station equipment at Pontiac to at least 1500 MVA (2510 Amps). | MI | MI | The Pontiac – Placid 345 kV circuit is projected to overload for a shutdown-plus-contingency that takes out Blackfoot – Madrid 345 kV and Pontiac - Wixom 345 kV lines. | BRP |  |  | 2022-12-31 | 2022-12-31 | 345 | 0 | Y | 2705000 | Bottom-Up
A in MTEP19 | B>A | East | ITCT | 16009 | Northeast 120 kV - Upgrade KD Reactor | Upgrade the Northeast 120 kV reactor at position “KD”. | MI | MI | The Northeast 120 kV reactor at position “KD”, which connects to the Caniff – Northeast 120 kV line, is projected to overload for a shutdown-plus-contingency that takes out Caniff – Stephens 345 kV circuit and Waterman 230/120kV transformer. | BRP |  |  | 2022-12-31 | 2022-12-31 | 120 | 0 | Y | 1200000 | Bottom-Up
A in MTEP19 | B>A | East | ITCT | 16013 | Thetford – Jewell 345 kV Sag Remediation | Raise the sag limit on the Thetford – Jewell 345 kV line to at least 1537 MVA and upgrade equipment at Thetford 345 kV station. | MI | MI | The Thetford – Jewell 345 kV circuit is projected to overload for many contingencies, including a T-1 that takes out Bauer – Pontiac 345 kV line. The limiting element on this circuit are sag limit and equipment at Thetford 345 kV station. | BRP |  |  | 2020-06-05 | 2020-06-05 | 345 | 0 | Y | 700000 | Bottom-Up
A in MTEP19 | B>A | East | ITCT | 16014 | Jewell – Stephens 345 kV Sag Remediation | Completely remove the sag limit on the Jewell – Stephens 345 kV line and upgrade equipment at Stephens 345 kV station. | MI | MI | The Jewell – Stephens 345 kV circuit is projected to overload for a shutdown-plus-contingency that takes out Bismarck – Jewel 345 kV and St. Clair – Stephens 345 kV lines. The limiting element on this circuit are sag limit and equipment at Stephens 345 kV station. | BRP |  |  | 2022-12-31 | 2022-12-31 | 345 | 0 | Y | 5700000 | Bottom-Up
A in MTEP19 | B>A | East | ITCT | 16020 | Cut Skylark – Sloan 120 kV into Redrun | Cut the Skylark – Sloan 120 kV line into Redrun station with the installation of two new 120 kV breakers. Also, upgrade station equipment at Sterling and rebuild approximately 1.6 miles of 795 ACSR conductor on the 120 kV sections from Sterling to Mustang2 to Van Dyke2 tap with 1431 ACSR as part of this project. | MI | MI | The 2018 assessment identified many buses in region between Skylark and Sterling 120 kV stations that are projected to experience low voltages in shutdown-plus-contingency combinations that would take out the 120 kV feed from Northeast to Skylark and 230 kV feed from Jewell to Sterling. | BRP |  |  | 2022-12-31 | 2022-12-31 | 120 | 0 | Y | 4997000 | Bottom-Up
A in MTEP19 | B>A | East | ITCT | 16023 | Lincoln-Northeast-Northwest 120 kV Rebuild | Rebuild approximately 3.3 miles of underground cable on the Lincoln – Northeast – Northwest 120 kV circuit to 3500KCMIL, rebuild about 7.1 miles of overhead conductor to 1431 ACSR, and upgrade station equipment at Northeast and Northwest. | MI | MI | Multiple sections of the Lincoln – Northeast – Northwest 120 kV circuit are protected to overload for shutdown-plus-contingency and double-circuit-tower that take out the Pontiac – Placid 345 kV and Pontiac – Wixom 345 kV lines. The overloaded elements are 477 ACSR and 795 ACSR conductors, 1500 KCMI underground cables, and equipment at Northeast and Northwest 120 kV stations. | BRP |  |  | 2024-06-01 | 2024-06-01 | 120 | 0 | Y | 44155000 | Bottom-Up
A in MTEP19 | B>A | East | ITCT | 16025 | Trenton Channel 120 kV Capacitor | Install a three 18 MVAR capacitors at Trenton Channel 120 kV station. | MI | MI | There are numerous voltage issues in the region near River Rouge, Riverview, and Trenton Channel 120 kV stations. The main driving contingency for these voltage violations is the loss of the Navarre 230/120kV transformer and or the Brownstown 345/120kV transformer #301. | BRP |  |  | 2021-12-31 | 2021-12-31 | 120 | 0 | Y | 1030000 | Bottom-Up
A in MTEP19 | B>A | East | ITCT | 16026 | Ironton 120 kV Capacitor | Install a three 18 MVAR capacitors at Ironton 120 kV station. | MI | MI | There are numerous voltage issues in the region near River Rouge, Riverview, and Trenton Channel 120 kV stations. The main driving contingency for these voltage violations is the loss of the Navarre 230/120kV transformer and or the Brownstown 345/120kV transformer #301. | BRP |  |  | 2021-12-31 | 2021-12-31 | 120 | 0 | Y | 515 | Bottom-Up
A in MTEP19 | B>A | East | ITCT | 16027 | Riverview 120 kV Capacitor | Install a three 18 MVAR capacitors at Riverview 120 kV station. | MI | MI | There are numerous voltage issues in the region near River Rouge, Riverview, and Trenton Channel 120 kV stations. The main driving contingency for these voltage violations is the loss of the Navarre 230/120kV transformer and or the Brownstown 345/120kV transformer #301. | BRP |  |  | 2021-12-31 | 2021-12-31 | 120 | 0 | Y | 1260000 | Bottom-Up
A in MTEP19 | B>A | East | ITCT | 16028 | Caniff – Saturn 120 kV Sag Remediation | Raise the sag on the Caniff – Saturn 120 kV line to at least 218 MVA. | MI | MI | The Caniff – Saturn 120 kV circuit is projected to overload for breaker failure and shutdown-plus-contingency that involves the loss of the Bristol – Caniff 120 kV and or Caniff – Cortland 120 kV lines. The limiting equipment on this circuit is the sag limit. | BRP |  |  | 2021-12-31 | 2021-12-31 | 120 | 0 | Y | 250000 | Bottom-Up
A in MTEP19 | B>A | East | ITCT | 16029 | Caniff 120 kV – Upgrade KU & LBX Station Equipment | Upgrade the station equipment at Caniff 120 kV positions “KU” and “LBX”. | MI | MI | The 345/120kV transformer and phase shifter at Caniff are projected to be overloaded in the basecase, G-1, T-1, and numerous contingencies in the 2018 assessment. The limiting elements on this transformer branch are the equipment at Caniff 120 kV station. | BRP |  |  | 2021-12-31 | 2021-12-31 | 120 | 0 | Y | 360000 | Bottom-Up
A in MTEP19 | B>A | East | ITCT | 16064 | Brownstown - Trenton Channel #1 120 kV Rebuild | Rebuild approximately 3.9 miles of conductor on the Brownstown – Trenton Channel #1 120 kV to 2156 ACSR and upgrade the equipment at Brownstown 120 kV and Trenton Channel 120 kV stations. | MI | MI | The Brownstown – Trenton Channel #1 120 kV circuit is projected to be heavily overloaded for various contingencies, most of them involve the loss of Navarre 230/120kV transformer or Brownstown 345/120kV transformer #301. The limiting elements on this circuit are the conductors, sag limit, and equipment at both Brownstown and Trenton Channel 120 kV stations. | BRP |  |  | 2022-06-01 | 2022-06-01 | 345 | 0 | Y | 10315000 | Bottom-Up
A in MTEP19 | B>A | East | ITCT | 16624 | Mountain | DTE interconnection request. ITC will need to tap the Pontiac - Sunbird 120kV line and the Bloomfield - Sunbird 120kV line to provide transmission service to DTE's new Mountain station. DTE will install 2 120/13.2kV transformers to serve about 12.5 MVA of load. | MI | MI | The interconnection is for 12.5 MVA of new load. This load requires a new transmission source to avoid overloads on the DTE 13.2kV system. | Other |  | Load Growth | 2019-12-31 | 2021-03-31 | 120 | 0 | Y | 1910000 | Bottom-Up
A in MTEP19 | B>A | East | ITCT | 16644 | Sigma Interconnection | Sigma is a 120kV station in a straight bus configuration with two line breakers and a section breaker. ITCT will cut in the Bismarck - Lenox 120kV line for transmission service. DTE will install two 120/13.2 kV transformers with circuit switchers for high side protection. DTE bus 11 and bus 12 will be tied via an A.T.O. Sigma will serve about 28.7 MVA of load relocated from Grayling and Jewell. | MI | MI | DTE interconnection request. Sigma 120kV will serve 28.7 MVA of relocated and networked load on the DTE 13.2kV system. | Other |  | Load Growth | 2022-04-01 | 2022-04-01 | 120 | 0 | Y | 4490000 | Bottom-Up
A in MTEP19 | B>A | East | ITCT | 16744 | Midtown Expansion | ITCT will expand the Midtown 120kV GIS from the existing 4-breaker ring bus to a 5-breaker ring bus. | MI | MI | This is a DTE load interconnection request to connect an additional 120/13.2kV transformer, 7.3 MW of new load and 4.4 MW of relocated load to ITCT’s existing Midtown 120kV Gas Insulated Substation (GIS). | Other |  | Load Growth | 2020-12-31 | 2020-12-31 | 120 | 0 | Y | 7902000 | Bottom-Up
A in MTEP19 | B>A | East | ITCT | 17164 | Romeo 345 kV Project | Romeo 345 kV: - Close “HY” breaker at St. Clair to allow the 345/120kV step-down transformation at this station. Also, upgrade three 120 kV breakers at St. Clair due to the short-circuit impact. - Cut the existing Jewell – St. Clair #1 into J793 POI (north of Belle River) form a tie between J793 and St. Clair station. This also relocates one of the sink paths (Jewell) to J793 POI station, making it more balanced to the area. The cut-in will require approximately 0.8 miles of 345 kV double-circuit with new right-of-way. Also, remediate the sag between J793 POI and Jewell up to the conductor’s limit. - Construct a new 345 kV switching station (tentatively named Romeo) about 3 miles north of Jewell station. - Cut the existing Belle River – Pontiac 345 kV line into Romeo station. Raise the sag on Belle River – Romeo and Pontiac – Romeo 345 kV lines up to the conductor’s limit and upgrade terminal equipment at Pontiac 345 kV station. - Construct a new 345 kV circuit between Romeo and Jewell using the available, de-energized 345 kV line that is on common structures with Jewell – St. Clair #1 345 kV line. This is new circuit is approximately 3.2 miles long. - Rebuild approximately 4.1 miles of the Hamlin – Spokane 120 kV line to 1431 ACSR. The rebuild is to use 230 kV construction on future double-circuit structures with OPGW. | MI | MI | The Belle River – St. Clair 345 kV, Belle River – Lenox 345 kV, Jewell – Lenox 345 kV, Jewell – St. Clair #1 345 kV, and St. Clair – Stephens 345 kV lines are projected to overload under various contingencies. The driving reason for these overloads in the area are due to the loss of generation on the 120 kV side of St. Clair plus the addition of J793 (Blue Water) on the 345 kV network in the same vicinity. Without the 120 kV source at St. Clair to help support the loads in the Oakland region, most of the output from Belle River and J739 are diverted toward the sinks southwest of them through the step-downs at Bismarck, Jewell, Stephens, and Lenox. The power flow path consequently stresses the Belle River – St. Clair 345 kV, Belle River – Lenox 345 kV, Jewell – Lenox 345 kV, Jewell – St. Clair #1 345 kV, and St. Clair – Stephens 345 kV lines and eventually overloads them under various contingencies. The overloaded scenarios are worse in models importing power from IESO to ITCT. According to ITC’s internal models, this import adds another ~1,200 MW to the 345 kV side of St. Clair. | BRP |  |  | 2023-12-31 | 2023-12-31 | 345 | 0 | Y | 52580000 | Bottom-Up
A in MTEP19 | B>A | East | ITCT | 17544 | Belle River - Lenox 345 kV Sag Remediation | Fully remediate the sag on the Belle River - Lenox 345kV line up to its conductor's limit. | MI | MI | The Belle River – Lenox 345 kV circuit is projected to overload for numerous contingencies, including a T-1 that takes out Belle River – St. Clair 345 kV line. The overloaded facilities are the 2-954 ACSR conductor, sag limit, and station equipment at Belle River 345 kV. | BRP |  |  | 2023-12-31 | 2023-12-31 | 345 | 0 | Y | 1500000 | Bottom-Up
A in MTEP19 | B>A | East | ITCT | 17545 | Jewell – Lenox 345 kV Sag Remediation | Remediate the sag limit on the Jewell – Lenox 345 kV line to at least 1500 MVA (2510 Amp). | MI | MI | The Jewell – Lenox 345 kV circuit is projected to overload for numerous contingencies, including a T-1 that takes out Belle River – St. Clair 345 kV line. The overloaded facilities are the 2-954 ACSR conductor, sag limit, and equipment at Jewell and Lenox 345 kV stations. | BRP |  |  | 2023-12-31 | 2023-12-31 | 345 | 0 | Y | 520000 | Bottom-Up
A in MTEP19 | B>A | East | ITCT | 17630 | 120 kV Cable Reactors | Install 1% reactors on the Caniff – Cortland, Caniff – Bristol, and Caniff – Cyril 120 kV lines | MI | MI | High flows and overloads were seen on the Caniff – Bristol 120 kV, Caniff – Cortland 120 kV, and Caniff – Cyril 120 kV lines for normal, N-1 and N-1-1 contingencies at peak and shoulder peak conditions. These three underground cables are in parallel with each other and a 120 kV overhead line. Because of the significantly lower impedances on the cables compared to the overhead conductor, most of the power flows through the cables instead of the overhead path creating an unbalanced system flow in the area. This project creates a better balance of system flows in the area by re-directing more power to flow down the 120 kV overhead path and relieves the overloads on the cables. | BRP |  |  | 2023-06-01 | 2023-06-01 | 120 | 0 | Y | 4500000 | Bottom-Up
A in MTEP19 | B>A | East | ITCT, METC | 15878 | Monroe - Lallendorf 345 kV Sag Remediation | Completely remove the sag limit on the Monroe – Lallendorf 345 kV line (ITCT side). | MI | MI | The Monroe – Lallendorf 345 kV line is projected to be overloaded for a shutdown-plus-contingency that takes out Brownstown – Monroe 345 kV and Monroe – Wayne 345 kV circuits. The identified overloaded equipment on this circuit is the sag limit. The thermal violations are found on all cases in the 2018 assessment. | BRP |  |  | 2021-12-31 | 2021-12-31 | 345 | 0 | Y | 1184000 | Bottom-Up
A in MTEP19 | B>A | East | METC | 13957 | Sternberg WPSC 138kV Connection | Expand METC's Sternberg 138kV station to a ring bus to connect a new WPSC 138kV circuit (to Casanova). | MI | MI | WPSC MTEP17 Appendix A project 12203, 138kV Voltage Conversion, requires a new connection to Sternberg. A ring bus configuration will improve the reliability to all utilities connecting to Sternberg (METC, Consumers Energy, Wolverine Power, Grand Haven) by eliminating the possibility of a single transmission station equipment failure outaging the entire station. | Other |  | Reliability | 2023-06-01 | 2023-06-01 | 138 | 0 | Y | 4160000 | Bottom-Up
A in MTEP19 | B>A | East | METC | 14824 | Shale 138 kV Station | Rebuild Saginaw River 138 kV station at a new site ~1.5 miles to the west. The new 138 kV station to be built will be called Shale. Acquire new property as necessary and install (12) 138 kV, 3000 A breakers with at least 40 kA interrupting capability in a four-row, breaker-and-a-half scheme configuration for this new station. The summer emergency rating of all new equipment should be no less than 800 MVA/3347 Amps (similar to recently constructed 138 kV stations). Utilize 954 ACSR conductor to reconfigure the following lines in to Shale: • Lawndale – Saginaw River 138 kV (Bay Road – Saginaw River 138 kV section) • Bullock – Saginaw River 138 kV (Laundra Tap – Saginaw River 138 kV section) • Au Sable 138 kV (Almeda Tap – Saginaw River 138 kV section of Twining – Saginaw River 138 kV) • Monitor – Saginaw River 138 kV • Weadock – Saginaw River 138 kV • Grey Iron – Saginaw River 138 kV • Karn – Saginaw River 138 kV to create eight new lines as follows: • Lawndale – Shale 138 kV • Bullock – Shale 138 kV • Au Sable 138 kV (Twining – Shale 138 kV) • Monitor – Shale 138 kV • Weadock – Shale 138 kV • Saginaw River – Shale 138 kV • Grey Iron – Shale 138 kV • Karn – Shale 138 kV At the existing Saginaw River site, remove and scrap the following equipment: • The breakers at Positions 188, 377, 488, 500, and 977. • The disconnect switches at Positions 182, 184, 185, 186, 275, 276, 375, 376, 377-bus, 377-line, 475, 476, 485, 486, 488-bus, 488-line, 488-bypass, 505, 506, 975, 976, 977-bus, and 977-line. • All steel, bus, hardware, free insulators, conductors, arresters, etc. Salvage, place in inventory, and reuse the following equipment at other locations: • The breakers at Positions 177, 277, and 477. • The disconnect switches at Positions 107, 171, 173, 175, 176, 207, 271, 273, 407, 471, 407, 471, and 473. • The relay control building and relay control panel equipment. • Normal HS 100 KVA SSVT transformer and Alt. HS 100 KVA SSVT transformer. • The newer CCVT’s on the following 138 kV lines: Au Sable, Bullock, Lawndale, Karn, Grey Iron, Weadock, and Monitor. • The newer wave traps on the Karn 138 kV line. Consumers Energy will perform the work required inside Saginaw River station to connect their 138/46 kV Transformer #1 to the 138 kV. | MI | MI | The Saginaw River 138 kV station is a mid-1920’s legacy station that was acquired from Consumers Energy as part of the METC acquisition. Much of the equipment has been in-service for several decades and has been identified as being in poor condition, a source of failure, and a safety hazard by the Asset Management Department at ITC. Furthermore, the configuration of the station also makes it difficult to perform routine maintenance on equipment as well. Some specific examples of the concerns are as follows: • Based on old blueprints found inside the original control house on the third floor, the oldest original, vintage infrastructure dates back to approximately the mid- 1920’s. The oldest oil circuit breakers are 1958 vintage and it’s assumed that the switches, insulators, and strain bus are approximately the same age. • There are known issues with aged, failing insulators. Visual inspections confirm that hundreds of old cap and pin insulators used in horizontal and strain configurations are cracked. Several have been blown by the wind and broke. They either were left hanging, or fell to the ground. In 2013, according to ULC operators, there was a near safety miss as horizontal insulators broke and fell to the ground. • There is a growing concern regarding the lack of proper, physical 138 kV bus inspections. Per legacy information from Consumers Energy, the last bus inspection was performed on June 1, 1994. Some key detractors to routine bus inspections are the sequencing of shutdowns (two lines at a time), hanging personal grounds in tight clearances, and lack of bus sectionalizing. o There is a 120 ft. working height associated with the bus work and limited space exists to set up equipment. The 8 ft. clearance between the Blue and White buses is an inadequate amount of space for a crane and personnel to work in. o None of the buses contain sectionalizing switches. • The existence of bus conductor that is broken at the splice and just hanging while energized is a known problem and has caused the ampacity rating of the existing copper bus to be unknown. • Spare parts for the older bus disconnects are unavailable. The Karn 138 kV line is an example. • There are also clearance issues when sparing/bypassing a breaker in order to inspect it since the bypass disconnects are located just above the bushings. • Future breaker replacements may require additional equipment to be dismantled or removed from service to get old equipment out. For example, the breaker at Position 500 is approximately 3-4 ft. away from the breaker at Position 977. • There are crumbling foundations and woodchucks are burrowing under cement breaker pads. • Unknown subgrade structures containing duct banks encased in cement were discovered while upgrading the Monitor 138 kV line in the Fall of 2016. • The access driveway is always flooded in the spring time with 1 ft. of water (photographic evidence exists in exception reports). | Other |  | Age and Condition | 2022-12-31 | 2022-12-31 | 138 | 0 | Y | 20000000 | Bottom-Up
A in MTEP19 | B>A | East | METC | 15719 | Bingham 138 kV Bus Rebuild | Rebuild the 138 kV portion of Bingham Substation to a breaker-and-a-half design with five breakers | MI | MI | Bingham Substation is a non-standard design, single bus station with three line exits, a transformer bank, and a capacitor bank. All three of the circuit breakers are identified as needing replacement. A breaker-and-a-half design will improve reliability, allowing for breaker maintenance without interruption of the transmission network, and limit the impact of breaker failure contingencies. | Other |  | Reliability | 2022-06-01 | 2022-06-01 | 138 | 0 | Y | 7500000 | Bottom-Up
A in MTEP19 | B>A | East | METC | 15736 | Butters Interconnection | New interconnection in Coldwater, MI. Butters will be a 138kV station with 4 breakers in a ring bus configuration. The Coldwater - Michigan Ave 138kV line will be looped in to provide transmission service. Coldwater will install 2 138/13.8 kV transformers to serve 21.75 MW of load | MI | MI | Local load growth will cause overloading on Coldwater's System. Coldwater needs another transmission source. | Other |  | Load Growth | 2020-12-31 | 2020-12-31 | 138 | 0 | Y | 6080000 | Bottom-Up
A in MTEP19 | B>A | East | METC | 15738 | Brooks Industrial | Interconnection request from the City of Marshall for transmission service. METC will build Brooks Industrial 138kV station as a breaker and half station with 5 breakers in a ring bus configuration. Brooks Industrial 138kV will be fed by installing 3.5 miles of new line to loop in the Verona - Marshall 138kV line. | MI | MI | A new industrial growth adds about 85MVA to the City of Marshall's distribution system causing many overloads. A new transmission feed is needed to provide relieve to the City of Marshall's distribution network. | Other |  | Load Growth | 2021-12-01 | 2021-12-01 | 138 | 0 | Y | 15700000 | Bottom-Up
A in MTEP19 | B>A | East | METC | 15740 | Stover 138 kV Circuit Switcher 256 Replacement | Replace Stover 138 kV circuit switcher 256 with a synchronous circuit breaker capable of interrupting at least 40 kA. | MI | MI | The 2018 ITC short circuit analysis demonstrates that the Stover 138 kV circuit switcher 256 is at risk of having to interrupt faults as high as 98.3%of its capability. | Other |  | Reliability | 2020-12-31 | 2020-12-31 | 138 | 0 | Y | 475000 | Bottom-Up
A in MTEP19 | B>A | East | METC | 15749 | Abbe Tap - Hillman Tap 138 kV Sag Remediation | The proposed solution is to remediate the sag limit on the Abbe Tap – Hillman Tap 138 kV section of the Airport – Mio 138 kV line to increase its summer emergency rating to a minimum of 91 MVA/382 Amps. | MI | MI | The Abbe Tap – Hillman Tap 138 kV section of the Airport – Mio 138 kV line is projected to become overloaded for shutdown plus contingency scenarios involving the Livingston – Gallagher – Tittabawassee 345 kV line and either the Bagley 1 Tap – Gaylord 138 kV, Bagley 1 Tap – Bagley 2 Tap 138 kV, or the Gaylord – Livingston 138 kV facilities. The overloads were identified in the 2020 and 2023 near-term peak load models with flow to IESO across the Michigan-Ontario interface. | BRP |  |  | 2021-12-31 | 2021-12-31 | 138 | 0 | Y | 590000 | Bottom-Up
A in MTEP19 | B>A | East | METC | 15750 | Saginaw River - Weadock 138 kV Sag Remediation | The proposed solution is to remediate the sag limit on the Saginaw River – Weadock 138 kV line to increase its summer emergency rating to a minimum of 159 MVA/667 Amps. | MI | MI | The Saginaw River - Weadock 138 kV line is projected to become overloaded for shutdown plus contingency scenarios involving the Monitor – Saginaw River 138 kV line and any one of the following facilities: Tittabawassee - Wackerly 138 kV, Letts Road Tap – Wackerly 138 kV, or Claremont – Holland 138 kV. The overloads were identified in the 2020, 2023, and 2028 peak load models with the Ludington units generating and flow to IESO across the Michigan-Ontario interface. | BRP |  |  | 2021-12-31 | 2021-12-31 | 138 | 0 | Y | 276000 | Bottom-Up
A in MTEP19 | B>A | East | METC | 15754 | Mio Dam - Plywood Tap 138 kV Sag Remediation | The proposed solution is to remediate the sag limit on the Mio Dam – Lewiston Tap 138 kV section of the Gaylord – Mio Dam 138 kV line to increase its summer emergency rating to a minimum of 147 MVA/615 Amps and remediate the sag limit on the Lewiston Tap – Plywood Tap 138 kV section of the Gaylord – Mio Dam 138 kV line to increase its summer emergency rating to a minimum of 147 MVA/615 Amps. | MI | MI | The Mio Dam – Lewiston Tap 138 kV and Lewiston Tap – Plywood Tap 138 kV sections of the Gaylord – Mio Dam 138 kV line are projected to become overloaded for shutdown plus contingency scenarios involving the Livingston – Gallagher – Tittabawassee 345 kV line and one of a number of other transmission facilities. The overloads were identified in the 2023 near-term peak and off-peak load models with the Ludington units generating and flow is to IESO across the Michigan-Ontario interface. | BRP |  |  | 2021-12-31 | 2021-12-31 | 138 | 0 | Y | 875000 | Bottom-Up
A in MTEP19 | B>A | East | METC | 15755 | MCV - Tittabawassee #2 345 kV Rebuild | The proposed solution is to rebuild the entire ~2.5 mile-long MCV – Tittabawassee 2 345 kV line that is comprised of 2156 ACSR conductor utilizing 2-1431 ACSR conductor and upgrade station equipment at both MCV and Tittabawassee. | MI | MI | The MCV – Tittabawassee 2 345 kV line is projected to become overloaded for numerous contingency types with the most severe loadings caused by shutdown plus contingencies involving the MCV – Tittabawassee 1 345 kV line plus one of a number of other transmission facilities. The overloads were identified in the 2020, 2023, and 2028 peak load models with the Ludington units generating regardless of the flow across the Michigan-Ontario interface. | BRP |  |  | 2023-12-31 | 2023-12-31 | 345 | 0 | Y | 10500000 | Bottom-Up
A in MTEP19 | B>A | East | METC | 15756 | MCV – Tittabawassee #1 345 kV Rebuild | The proposed solution is to rebuild the entire ~2.5 mile-long MCV – Tittabawassee 1 345 kV line that is comprised of 2156 ACSR conductor utilizing 2-1431 ACSR conductor and upgrade station equipment at both MCV and Tittabawassee. | MI | MI | The MCV – Tittabawassee 1 345 kV line is projected to become overloaded for numerous contingency types with the most severe loadings caused by shutdown plus contingencies involving the MCV – Tittabawassee 2 345 kV line plus one of a number of other transmission facilities. The overloads were identified in the 2020, 2023, and 2028 peak load models with the Ludington units generating regardless of the flow across the Michigan-Ontario interface. | BRP |  |  | 2022-12-31 | 2023-12-31 | 345 | 0 | Y | 10228000 | Bottom-Up
A in MTEP19 | B>A | East | METC | 15790 | Hemphill - Thetford 138 kV Sag Remediation | The proposed solution is to remediate the sag limit on the Hemphill – Thetford 138 kV line and reset or replace the thermal relaying at Hemphill to increase the line’s summer emergency rating to a minimum of 306 MVA/1280 Amps. | MI | MI | The Hemphill – Thetford 138 kV line is projected to become overloaded for shutdown plus contingency scenarios involving the Garfield Avenue – Hemphill 138 kV line and either the Delaney – Thetford 138 kV line or the CE-owned Delaney 138 kV bus. The overloads were identified in the 2020, 2023, and 2028 peak load models with the Ludington units generating regardless of the directional flow across the Michigan-Ontario interface. | BRP |  |  | 2022-12-31 | 2022-12-31 | 138 | 0 | Y | 386000 | Bottom-Up
A in MTEP19 | B>A | East | METC | 15791 | Hemphill – Sabine 138 kV Rebuild | The proposed solution is to rebuild ~2.8 miles of the Hemphill – Sabine 138 kV line that is comprised of 336 ACSR conductor only utilizing 954 ACSR conductor and remediate the sag limit on 477 ACSR conductor to increase the line’s summer emergency rating to a minimum of 199 MVA/832 Amps. | MI | MI | The Hemphill – Sabine 138 kV line is projected to become overloaded for numerous contingency types with the most severe loadings caused by shutdown plus contingencies involving either the Hemphill – Porter Tap 138 kV or Blinton – Porter Tap 138 kV facility of the Halsey – Hemphill 138 kV line plus one of a number of other transmission facilities. The overloads were identified in the 2020, 2023, and 2028 peak load models with the Ludington units generating and the flow is mainly to ITCT across the Michigan-Ontario interface. | BRP |  |  | 2023-06-01 | 2023-06-01 | 138 | 0 | Y | 4810000 | Bottom-Up
A in MTEP19 | B>A | East | METC | 15792 | Halsey - Sabine 138 kV Rebuild | The proposed solution is to rebuild the entire ~5.3 mile-long Halsey – Sabine 138 kV line that is comprised of 336 ACSR conductor utilizing 954 ACSR conductor and upgrade the 336 ACSR line entrance at Halsey. | MI | MI | The Halsey – Sabine 138 kV line is projected to become overloaded for numerous contingency types with the most severe loadings caused by shutdown plus contingencies involving the Hemphill – Porter Tap 138 kV facility of the Halsey – Hemphill 138 kV line plus one of a number of other transmission facilities. The overloads were identified in the 2020, 2023, and 2028 peak load models with the Ludington units generating and flow is mainly to ITCT across the Michigan-Ontario interface. | BRP |  |  | 2024-06-01 | 2024-06-01 | 138 | 0 | Y | 6730000 | Bottom-Up
A in MTEP19 | B>A | East | METC | 15793 | Gaylord - Livingston 138 kV Rebuild | The proposed solution is to rebuild ~1.3 miles of the Gaylord – Livingston 138 kV line that is comprised of 266 ACSR conductor only utilizing 954 ACSR conductor on 230 kV double-circuit structures. | MI | MI | The Gaylord – Livingston 138 kV line is projected to become overloaded for shutdown plus contingencies involving the Livingston – Gallagher – Tittabawassee 345 kV line and another transmission facility. The overloads were identified in the 2020 and 2023 85% peak load models with the Ludington units generating and flow is to IESO across the Michigan-Ontario interface. | BRP |  |  | 2023-06-01 | 2023-06-01 | 138 | 0 | Y | 1745000 | Bottom-Up
A in MTEP19 | B>A | East | METC | 15794 | Garfield Avenue – Karn 138 kV Rebuild | The proposed solution is to rebuild ~32.2 miles of the Garfield Avenue – Karn 138 kV line that is comprised of 3/0 copper conductor only utilizing 1431 ACSR conductor and remediate the sag limit on ~14.8 miles of 1431 ACSR conductor to increase the summer emergency rating to a minimum of 223 MVA/934 Amps. | MI | MI | The Garfield Avenue – Karn 138 kV line is projected to become overloaded for shutdown plus contingencies involving either the Karn – Saginaw River 138 kV or Karn – Manning 138 kV line plus another transmission facility. The overloads were identified in the 2020, 2023, and 2028 peak and off-peak load models for all Ludington output scenarios regardless of the directional flow across the Michigan-Ontario interface. | BRP |  |  | 2023-12-31 | 2023-12-31 | 138 | 0 | Y | 40000000 | Bottom-Up
A in MTEP19 | B>A | East | METC | 15797 | Donaldson Creek - White Lake 138 kV Sag Remediation & Equipment Upgrade | The proposed solution is to remediate the sag limit on the Donaldson Creek – White Lake 138 kV line and upgrade station equipment at White Lake to increase the line’s summer emergency rating to a minimum of 171 MVA/715 Amps. | MI | MI | The Donaldson Creek – White Lake 138 kV line is projected to become overloaded for shutdown plus contingency scenarios involving any one of the following lines plus another transmission facility: Ludington – Meyer 345 kV, Ludington – Tallmadge 1 345 kV, Cobb – Tallmadge 1 138 kV, Polkton - Meyer 138 kV, Kenowa – Ludington 1 345 kV, and Kenowa – Ludington 2 345 kV. The overloads were identified in the 2020 and 2023 near-term peak and shoulder peak load models with the Ludington units generating while flow is to ITCT across the Michigan-Ontario interface. | BRP |  |  | 2021-12-31 | 2021-12-31 | 138 | 0 | Y | 1176800 | Bottom-Up
A in MTEP19 | B>A | East | METC | 15798 | Cornell - Goss 138 kV Sag Remediation | The proposed solution is to remediate the sag limit on the Cornell – Goss 138 kV line to increase its summer emergency rating to a minimum of 277 MVA/1158 Amps. | MI | MI | The Cornell – Goss 138 kV line is projected to become overloaded for a fault on the Claremont 500 138 kV breaker or for shutdown plus contingency scenarios involving either the Claremont – Cornell 1 or 2 138 kV line plus another transmission facility. The overloads were identified in the 2020, 2023, and 2028 peak load models with either zero flow or flow to ITCT across the Michigan-Ontario interface while the Ludington units are generating. | BRP |  |  | 2021-12-31 | 2021-12-31 | 138 | 0 | Y | 581000 | Bottom-Up
A in MTEP19 | B>A | East | METC | 15800 | Bass Creek - Black River 138 kV Rebuild | The proposed solution is to rebuild 3.77 miles of the Bass Creek – Black River using 954 ACSR conductor with single circuit steel structures. | MI | MI | The Bass Creek – Black River 138kV line is projected to marginally overload for the shutdown plus contingency involving Blendon – Campbell 138kV line and Ludington – Pere Marquette 345kV line. The identified overloaded equipment on this circuit is the conductor. The thermal violations are only found on off peak cases. | BRP |  |  | 2023-12-31 | 2023-12-31 | 138 | 0 | Y | 4450000 | Bottom-Up
A in MTEP19 | B>A | East | METC | 15801 | Beals Road - Stamping Plant 138 kV Rebuild | The Stamping Plant – Beals Road 138kV circuit is projected to overload for shutdown plus contingency scenarios involving Beals – Wealthy and Gaines – Henry 138kV lines. The identified overloaded equipment on this circuit is the conductor. The thermal violations are found on peak and off peak cases. | MI | MI | The proposed solution is to rebuild 1.22 miles of the Stamping Plant – Beals Road 138kV circuit using 954 ACSR conductor with single circuit steel structures. | BRP |  |  | 2023-06-01 | 2023-06-01 | 138 | 0 | Y | 2500000 | Bottom-Up
A in MTEP19 | B>A | East | METC | 15802 | Beals Road - Wealthy 138 kV Rebuild | The proposed solution is to rebuild 3.15 miles, 6-wire 336 ACSR section of the Wealthy-Beals Road 138kV circuit using 1431 ACSR conductor with single circuit steel structures. | MI | MI | The Beals Road – Wealthy 138kV circuit is projected to overload for a shutdown plus contingency scenario involving the Gaines – Rooselvelt and Gaines – Vergennes 345kV lines. The identified overloaded equipment on this circuit is the conductor. The thermal violations are only found on peak cases. | BRP |  |  | 2024-06-01 | 2024-06-01 | 138 | 0 | Y | 4158000 | Bottom-Up
A in MTEP19 | B>A | East | METC | 15803 | Gaines - Meadowbrooke 138 kV Rebuild | The proposed solution is to rebuild 0.09 mile Gaines – Meadowbrooke section of the Gaines – Plaster Creek 138kV circuit using 2156 ACSR with steel structures and replace terminal equipment. | MI | MI | The Gaines – Meadowbrooke section of the Gaines – Plaster Creek 138kV circuit is projected to overload for various scenarios, the worst involving the shutdown plus contingency involving both Vergennes 345/138 kV transformers. The identified overloaded equipment on this circuit is the conductor and terminal equipment. The thermal violations are only found on peak cases. | BRP |  |  | 2024-12-31 | 2024-12-31 | 138 | 0 | Y | 486000 | Bottom-Up
A in MTEP19 | B>A | East | METC | 15804 | Gaines - Stamping Plant 138kV Rebuild | The Gaines – Stamping Plant 138kV circuit is projected to overload for shutdown plus contingency scenarios involving Beals – Wealthy and Gaines – Henry 138kV lines. The identified overloaded equipment on this circuit is the conductor. The thermal violations are found on peak and off peak cases. | MI | MI | The proposed solution is to rebuild 10.98 miles of the Gaines – Stamping Plant 138kV circuit using 954 ACSR conductor with single steel structures. | BRP |  |  | 2024-06-01 | 2024-06-01 | 138 | 0 | Y | 16000000 | Bottom-Up
A in MTEP19 | B>A | East | METC | 15805 | Spaulding - Vergennes 138 kV Rebuild | The proposed solution is to rebuild 7.17 miles the Vergennes – Spaulding circuit using 1431 ACSR conductor with single circuit steel structures. Also replace terminal equipment at Spaulding and Vergennes. | MI | MI | The Spaulding – Vergennes 138kV circuit is projected to overload for a shutdown plus contingency involving both Gaines 345/138 kV transformers. The identified overloaded equipment on this circuit is the conductor and terminal equipment at Spaulding and Vergennes. The thermal violations are only found on peak cases. | BRP |  |  | 2024-06-01 | 2024-06-01 | 138 | 0 | Y | 6200000 | Bottom-Up
A in MTEP19 | B>A | East | METC | 15806 | Cobb - Meyer 138 kV Rebuild | Rebuild approximately 5.74 miles of 477 ACSR conductor to 1431 ACSR conductor from Meyer to Arthur Jct. of the Meyer – Cobb 138kV circuit. The rebuild will be 138kV construction using future double – circuit steel structures with OPGW. Also remediate sag on the Cobb – Arthur Jct. section to conductor limit of 908 Amps (217 MVA). | MI | MI | The Cobb – Meyer 138kV line is projected to severely overload under various contingency scenarios, the worst involving the shutdown plus contingency scenarios of the Cobb – Tallmadge #1 138kV line and either the Ludington – Pere Marquette 345kV or Pere Marquette 345/138 kV Transformer 2. The identified overloaded equipment on this circuit is the conductor on the Meyer – Wilson St. circuit and sag limit on the Wilson St. – Cobb 138kV circuit. The thermal violations are only found on peak and off peak cases. | BRP |  |  | 2024-06-01 | 2024-06-01 | 138 | 0 | Y | 7400000 | Bottom-Up
A in MTEP19 | B>A | East | METC | 15808 | Black River - Tyler 138 kV Reconductor | The proposed solution is to reconductor ~10.91 miles of the Black River – Tyler using 954 ACSS conductor and also remove station equipment at Black River and Tyler. | MI | MI | The Black River – Tyler 138kV line is projected to overload under various contingency scenarios, the worst involving the shutdown plus contingency scenario of the Campbell – Black River and Industrial – Soholn 138kV lines. The identified overloaded equipment on this circuit is the conductor and station equipment. The thermal violations are only found on off peak cases. | BRP |  |  | 2023-12-31 | 2023-12-31 | 138 | 0 | Y | 5300000 | Bottom-Up
A in MTEP19 | B>A | East | METC | 15833 | Bagley Tap - Gaylord 138 kV Rebuild | Rebuild the entire ~1.2 mile-long Bagley Tap – Gaylord 138 kV section of the ~40.4 mile-long Gaylord – Mio Dam 138 kV line. Pre-build it to 230 kV construction to facilitate potential future 230 kV expansion in northern Michigan. Replace the existing assets (all structures, 266 ACSR conductor, and the 266 ACSR line entrance at Gaylord) with new double-circuit structures that are designed for 954 ACSR conductor on each side and install this conductor along with OPGW for the existing line only. | MI | MI | The Bagley Tap – Gaylord 138 kV section of the Gaylord – Mio Dam 138 kV line is projected to become overloaded for shutdown plus contingencies involving either the Livingston – Gallagher – Tittabawassee 345 kV line or the Gallagher 345/138 kV Transformer #2 plus another transmission facility. The overloads were identified in the 2023 peak and off-peak load models with the Ludington units generating and the flow is to IESO across the Michigan-Ontario interface. | BRP |  |  | 2024-06-01 | 2024-06-01 | 138 | 0 | Y | 1584000 | Bottom-Up
A in MTEP19 | B>A | East | METC | 15836 | Bell Road - Claremont 138 kV Sag Remediation | Remediate the sag limit on ~3.0 miles of 477 ACSR conductor of the Bell Road – Claremont 138 kV section of the Claremont – Cornell 2 138 kV line to at least the planned target summer normal/summer emergency rating of 188 MVA/787 Amps. | MI | MI | The Bell Road – Claremont 138 kV section of the Claremont – Cornell 2 138 kV line is projected to become overloaded for shutdown plus contingency scenarios involving either the Cornell – Goss 138 kV, Claremont – Layton 138 kV, Cornell – Layton 138 kV, or the Claremont – Cornell 1 138 kV line plus another transmission facility. The overloads were identified in the 2020, 2023, and 2028 peak load models with either zero flow or flow to ITCT across the Michigan-Ontario interface while the Ludington units are generating. | BRP |  |  | 2022-12-31 | 2022-12-31 | 138 | 0 | Y | 410000 | Bottom-Up
A in MTEP19 | B>A | East | METC | 15839 | AKT (Atlanta - Karn - Thetford) Tap - Karn 138 kV Sag Remediation | Remediate the sag limit on the entire ~15.3 mile-long length of 1431 ACSR conductor of the AKT (Atlanta - Karn - Thetford) Tap - Karn 138 kV section of the Atlanta - Karn - Thetford 138 kV line and upgrade terminal equipment at Karn to achieve at least the planned target summer normal/summer emergency rating of 371 MVA/1552 Amps. | MI | MI | The AKT (Atlanta - Karn - Thetford) Tap - Karn 138 kV section of the Atlanta - Karn - Thetford 138 kV line is projected to become overloaded for shutdown plus contingency scenarios involving the Karn – Manning 138 kV and Karn – Saginaw River 138 kV lines. The overloads were identified in the 2020, 2023, and 2028 peak and shoulder peak load models regardless of the directional flow across the Michigan-Ontario interface or the Ludington generating/pumping condition. | BRP |  |  | 2022-12-31 | 2022-12-31 | 138 | 0 | Y | 803000 | Bottom-Up
A in MTEP19 | B>A | East | METC | 15852 | Cornell - Tihart 138kV Sag Remediation | The proposed solution is to remediate sag limit on the Cornell – Tihart 138kV circuit to increase its summer emergency rating to a minimum of 182 MVA/763 Amps on the Bennington – Scenic Lake and Van Atta – Scenic Lake sections to increase its summer emergency rating to a minimum of 191 MVA/801 Amps. | MI | MI | The Cornell – Tihart 138kV circuit is projected to become marginally overloaded for a shutdown plus contingency involving the Bauer – Pontiac and Thetford – Jewel 345kV lines. The identified overloaded equipment on this circuit is the sag limit. The thermal violations are found on peak cases. | BRP |  |  | 2021-12-31 | 2021-12-31 | 138 | 0 | Y | 425000 | Bottom-Up
A in MTEP19 | B>A | East | METC | 15893 | Batavia - Morrow 138 kV Rebuild | Rebuild 5.18 miles of the Morrow – Parkville section of the Batavia – Morrow 138kV circuit using 954 ACSR conductor with steel structures and also remediate sag limit on the 795 ACSR section of the circuit to a minimum of 210 MVA/880 Amps. Also replace terminal equipment at Morrow station. | MI | MI | The Morrow – Parkville section of the Batavia – Morrow 138kV circuit is projected to overload for contingency scenarios involving the Beecher – Moore Road and Verona – Wagner 138kV lines. The identified overloaded equipment on this circuit are the conductor, sag limit, and terminal equipment at Morrow station. The thermal violations are found on peak cases. | BRP |  |  | 2024-12-31 | 2024-12-31 | 138 | 0 | Y | 5419000 | Bottom-Up
A in MTEP19 | B>A | East | METC | 15894 | METC Customer Interconnections - Year 2022 | Customer interconnection requests and retirements less than $1 million with in service dates in the year 2022. | MI | MI | Customer Requests are often in need of interconnection on an expedited basis. This blanket allows interconnection requests of smaller nature to be quickly studied and connected by METC. | Other |  | Other Local Needs | 2022-12-31 | 2022-12-31 | 138 | 0 | Y | 2500000 | Bottom-Up
A in MTEP19 | B>A | East | METC | 15899 | Campbell - Blendon 138kV Sag Remediation | Remediate sag limit on the Bill Mar – Port Sheldon section of the Campbell – Blendon 138kV circuit to increase its summer emergency rating to a minimum of 390 MVA/1633 Amps. | MI | MI | The Campbell – Blendon 138kV circuit is projected to overload for a shutdown plus contingency involving the Campbell – Roosevelt and Campbell – Tallmadge 345kV lines. The identified overloaded equipment on this circuit is the sag limit. The thermal violations are found on peak and off peak cases. | BRP |  |  | 2021-06-01 | 2021-06-01 | 138 | 0 | Y | 390000 | Bottom-Up
A in MTEP19 | B>A | East | METC | 15901 | Cornell - Claremont Sag Remediation | Remediate sag limit on the Cornell – Claremont 138kV circuit to increase its summer emergency rating to a minimum of 165 MVA/692 Amps on the Cornell – Layton section and also increase its summer emergency rating to a minimum of 203 MVA/850 Amps on the Claremont – Layton section. | MI | MI | The Cornell – Claremont 138kV circuit is projected to overload for a shutdown plus contingency involving the Claremont – Cornell #2 and Cornell – Goss 138kV lines. The identified overloaded equipment on this circuit is the sag limit. The thermal violations are found on peak cases. | BRP |  |  | 2021-06-01 | 2021-06-01 | 138 | 0 | Y | 1900000 | Bottom-Up
A in MTEP19 | B>A | East | METC | 15906 | Campbell - Black River 138kV Sag Remediation | Completely remove the sag limit on the Campbell – Black River circuit to conductor limit. | MI | MI | The Campbell – Black River 138kV circuit is projected to overload for a shutdown plus contingency involving the Industrial – Soholn and Tyler – Black River 138kV lines. The identified overloaded equipment on this circuit is the sag limit. The thermal violations are found on peak cases. | BRP |  |  | 2021-06-01 | 2021-06-01 | 138 | 0 | Y | 807000 | Bottom-Up
A in MTEP19 | B>A | East | METC | 15909 | Tallmadge - Tyler 138kV Sag Remediation | Remediate sag limit on the Tallmadge – Tyler 138kV circuit to increase its summer emergency rating to a minimum of 367 MVA/1535 Amps. | MI | MI | The Tallmadge – Tyler 138kV circuit is projected to overload for a shutdown plus contingency involving the Campbell – Roosevelt and Campbell – Tallmadge 345kV lines. The identified overloaded equipment on this circuit is the sag limit. The thermal violations are found on off peak cases. | BRP |  |  | 2021-06-01 | 2021-06-01 | 138 | 0 | Y | 5400000 | Bottom-Up
A in MTEP19 | B>A | East | METC | 15912 | Battle Creek - Verona #2 138kV Sag Remediation | Completely remove sag limit on the Battle Creek – Verona #2 138kV to conductor limit and also upgrade station equipment at Verona position 577 to increase its summer emergency rating to a minimum of 440 MVA/1839 Amps. | MI | MI | The Battle Creek – Verona #2 138kV line is projected to become marginally overloaded for contingency scenarios involving the Battle Creek – Verona #1 and Argenta – Verona 138kV lines. The identified overloaded equipment on this circuit are the sag limit and station equipment. The thermal violations are found on off peak cases. | BRP |  |  | 2021-12-31 | 2021-12-31 | 138 | 0 | Y | 186000 | Bottom-Up
A in MTEP19 | B>A | East | METC | 15913 | Morrow - Battle Creek #2 138kV Sag Remediation | Completely remove sag limit on the Lafayette – Morrow section of the Morrow – Battle Creek #2 138kV to conductor limit. | MI | MI | The Lafayette - Morrow section of the Morrow - Battle Creek #2 138kV line is projected to overload for shutdown plus contingency scenarios, the worst involving the Argenta – Battle Creek 345kV line and Morrow - Battle Creek 138kV line. The identified overloaded equipment on this circuit is the sag limit. The thermal violations are found on peak and off peak cases. | BRP |  |  | 2021-12-31 | 2021-12-31 | 138 | 0 | Y | 940000 | Bottom-Up
A in MTEP19 | B>A | East | METC | 15938 | Leoni - Parr Road 138kV Sag Remediation | Remediate sag limit on the Leoni – Parr Road 138kV line to increase its summer emergency rating to a minimum of 167 MVA/700 Amps. | MI | MI | The Leoni – Parr Road 138 kV line is projected to overload for shutdown plus contingency scenarios, the worst involving the Morocco 345/138kV transformer 2 and Leoni – Seamless 138 kV line. The identified overloaded equipment on this circuit is the sag limit. The thermal violations are found on peak cases. | BRP |  |  | 2021-06-01 | 2021-06-01 | 138 | 0 | Y | 725000 | Bottom-Up
A in MTEP19 | B>A | East | METC | 15942 | Cobb 138 kV Station Rebuild | rebuild Cobb 138 kV station at a new site approximately 3.9 miles to the east (Pine Creek) utilizing new equipment in a six-row, breaker-and-a-half scheme configuration. This solution is to avoid tripping many 138kV circuits for a fault on the 500 bus – tie circuit breaker. Acquire new property as necessary and install (17) 138 kV, 3000 A breakers with at least 40 kA (upgradable to 63kA) interrupting capability in a six-row, breaker-and-a-half scheme configuration for this new station. Redirect all circuits currently at the Cobb 138 kV station into the new 138 kV station and connect step-down transformers (TB) #7 and #8 via radial feeds into the new station. | MI | MI | Cobb 138kV station is a straight bus substation. There are seven METC’s 138kV lines, two CE’s 138kV lines, and CE’s 46kV network connect to METC system at Cobb. The 500 bus – tie circuit breaker fault at Cobb (outage of Cobb station) can cause thermal overloads and low voltages in the area. The Black River – Bass Creek and Bass Creek – Sternberg 138kV lines were identified to overload for this breaker fault. The thermal and voltage violations are found on peak and off peak cases. | BRP |  |  | 2023-12-31 | 2023-12-31 | 138 | 0 | Y | 23100000 | Bottom-Up
A in MTEP19 | B>A | East | METC | 15990 | METC Pole Top Switch Additions/Replacement Program 2021 | Installing, or replacing as appropriate, pole-top switches at tap points of circuits will provide the operational flexibility to sectionalize parts of the line to isolate faults or perform maintenance work on it without having to shut down the entire circuit. | MI | MI | Install or replace an existing a new 138 kV, 2-way, full-load-break pole top switch at various tap points | Other |  | Reliability | 2021-12-31 | 2021-12-31 | 138 | 0 | Y | 3600000 | Bottom-Up
A in MTEP19 | B>A | East | METC | 15996 | 2022 METC Asset Replacement Program | Replace aging and outdated equipment on a cycle that will ensure each piece of equipment is replaced near its expected end of life. Modern equipment can improve reliability, use state of the art technology, and typically will allow for longer maintenance intervals. New equipment is also commonly equipped with better monitoring and alarming functionality giving improved remote supervision. All of this will help to reduce overall maintenance costs. | MI | MI | Equipment that is past its expected design life, utilizes outdated functionality or whose failure rates and maintenance requirements have increased the potential for misoperations and higher maintenance costs associated with their ongoing use. | Other |  | Reliability | 2022-12-31 | 2022-12-31 | 345 | 138 | Y | 42000000 | Bottom-Up
A in MTEP19 | B>A | East | METC | 16002 | Four Mile 138 kV Station Rebuild | Rebuild Four Mile 138 kV station at a new site approximately half a mile to the west (Northridge) in a five row, breaker-and-a-half scheme configuration and redirect all circuits currently at the Four Mile 138 kV station into the new 138 kV station. Step-down transformers (TB) #1, #2, #3, and #4 will be connected radially to the new station via the existing 138 kV lines out of the Four Mile station. This new 138 kV station would reduce equipment failures, unplanned outages, and repair costs. In addition, it would enable routine maintenance and outages to be performed in a safe and efficient manner. | MI | MI | The Four Mile 138 kV station is an early-1950’s vintage station. The station high voltage electrical equipment has been in-service for several decades and has realized the end of its useful life. This equipment is dated (requires the use of operating practices that do not employ the safety measure designed in modern equipment), a source of failure, emergency maintenance, and in need of a wholesale replacement. The station was designed in accordance with design practices of the era. ITC and the industry’s design practices today - utilizing modern high voltage electrical equipment - produces a reliable, safe, accessible, and operationally flexible station. As it stands today, Four Mile station’s design and integrity makes it difficult to perform routine maintenance on equipment and presents challenges when conducting routine operations. Furthermore the present station design is such that a single faulted breaker will deenergize the entire station, dropping network load from 7 lines and 2 sub-transmission transformers. | Other |  | Reliability | 2022-12-31 | 2022-12-31 | 138 | 0 | Y | 16000000 | Bottom-Up
A in MTEP19 | B>A | East | METC | 16003 | Morocco-Whiting_Samaria-Whiting 138kV Rebuild | Rebuild approximately 10.3 miles of wood pole construction from Samaria to Whiting consolidating Samaria-Whiting and Morocco-Whiting into one corridor on 138kV double circuit steel poles with 954 ACSR conductor. The rebuild will be 138kV construction using double-circuit steel structures with 954 ACSR conductor on both Samaria - Whiting and Morocco – Whiting 138kV circuits. Reconductor (using 954 ACSR conductor) 0.41 mile remaining section of the Morocco – Whiting 138kV circuit and 1.1 mile remaining section of the Samaria – Whiting 138kV circuit. Also install OPGW from Whiting to existing splice box near Samaria. | MI | MI | The METC system relies heavily on both wood poles and steel lattice towers, many of which are 65 years of age or older. METC transmission structures may experience increasing failure rates that could degrade reliability on the system. Maintenance, partial rebuild, or complete rebuild activities need to be undertaken on aging circuits throughout the system in order to maintain acceptable levels of system reliability. ITC performed an analysis in 2017 to assess the METC and ITCT circuits based on 4 main factors: recent outage history, current maintenance needs, age and type of structures and circuit importance. The objective of the analysis was to assist ITC staff in identifying circuits that should be considered for rebuilding. While there is not a specific criteria used to determine when these assets reach their end of life, utilizing the factors described above helps to prioritize replacement of aging infrastructure across the ITC systems. Based on that criteria, the Morocco-Whiting 138kV circuit and Samaria-Whiting 138kV circuit are being recommended for a full line rebuild. Currently 37% of the total wood poles on these lines need to be replaced to due to age and are outstanding maintenance issue. Upon further investigation, a review of the 1948 grade C requirements concluded that 75% of existing wood pole structures should be replaced or modified due to overloading. Modification is not recommend with wood construction of this age. METC is recommending that these circuits be rebuilt in order to maintain the METC system at acceptable levels of system performance and to improve system reliability. | Other |  | Age and Condition | 2024-12-31 | 2024-12-31 | 138 | 0 | Y | 12100000 | Bottom-Up
A in MTEP19 | B>A | East | METC | 16067 | Bradley - Morrow 138 kV Rebuild | Rebuild 7.73 miles of the Bradley – Barry Jct. section of the Bradley – Morrow 138kV circuit using 954 ACSR conductor with single circuit steel structures. | MI | MI | The Bradley – Barry Jct. section of the Bradley – Morrow 138kV line is projected to overload for a shutdown plus contingency involving the Argenta – Tallmadge and Argenta – Meyer 345kV lines. The identified overloaded equipment on this circuit is the conductor. The thermal violations are found on peak and off peak cases. | BRP |  |  | 2023-12-31 | 2023-12-31 | 138 | 0 | Y | 7900000 | Bottom-Up
A in MTEP19 | B>A | East | METC | 16424 | J602 Network Upgrades | METC to install a 138kV breaker and disconnects at Goss 138kV station | MI | MI | J602 is a 200 MW wind farm that requested to interconnect to the METC Goss 138 kV station in the DPP-2016-AUG cycle. | GIP |  |  | 2021-09-01 | 2021-09-01 | 138 | 0 | Y | 784000 | Externally Driven
A in MTEP19 | B>A | East | WPSC | 9895 | Graves Crossing to Central Lake Rebuild | Rebuild the Graves Crossing to Central Lake 69kV line, install new poles and hardware with 336ACSR conductor | MI | MI | This 69kV transmission line segment was built in 1975. This line segment has 42% condemned, rotten tops, or damaged structures. Because there are so many poles in need of replacing, it falls within our condition based transmission line rebuild criteria to demolish the existing line and rebuild to our new standard configuration. | Other |  | Age and Condition | 2022-12-31 | 2022-12-31 | 69 | 0 | Y | 4080000 | Bottom-Up
A in MTEP19 | B>A | East | WPSC | 12220 | Portland to Clinton line rebuild | Rebuild line to 138kV design with 795ACSS conductor | MI | MI | Aging Infrastructure. Line was constructed in 1952 and currently has 31% condemned or damaged poles. Resolves Overloads of up to 110.9% seen in MTEP18 cycle. | BRP |  |  | 2022-12-31 | 2022-12-31 | 69 | 0 | Y | 7500000 | Bottom-Up
A in MTEP19 | B>A | East | WPSC | 15646 | Atlanta to Lewiston Rebuild | Rebuild and upgrade 12 miles of 69 kV to 138 kV design, 795ACSS conductor and OPGW. | MI | MI | Condition Based - Replace aging infrastructure. • Built in 1953, current age 65 years • 69 damaged poles • 20% of poles in need of replacement | Other |  | Age and Condition | 2021-12-31 | 2021-12-31 | 69 | 0 | Y | 6120000 | Bottom-Up
A in MTEP19 | B>A | East | WPSC | 15651 | Clinton to Wayland Rebuild | Rebuild and upgrade 41 miles of 69 kV line to 138 kV design, 795ACSS conductor and OPGW. | MI | MI | Condition Based - Replace aging infrastructure. • Oldest line section built in 1971 • 40 condemned and 210 damaged poles • 37% of poles in need of replacement Baseline Reliability – Under-voltage Resolve under-voltage conditions seen around Wayland with P2 and P6 contingencies | Other |  | Age and Condition | 2022-12-31 | 2022-12-31 | 69 | 0 | Y | 23700000 | Bottom-Up
A in MTEP19 | B>A | East | WPSC | 16104 | Altona to Pierson Rebuild | Rebuild and upgrade 14 miles of 69 kV line to 138 kV design, 795ACSS conductor and OPGW. | MI | MI | Project Driver: Condition Based - Replace aging infrastructure. • Line section built in 1953 • 16 condemned and 37 damaged poles • 35% of poles in need of replacement | Other |  | Age and Condition | 2022-12-31 | 2022-12-31 | 138 | 0 | Y | 7300000 | Bottom-Up
A in MTEP19 | B>A | East | WPSC | 16344 | Weidman 69kV Bus rebuild | Rebuild 69kV Bus at Weidman station | MI | MI | Rebuild the existing 69kV bus to accommodate additional capacity at station. | Other |  | Reliability | 2020-12-31 | 2020-12-31 | 69 | 0 | Y | 170000 | Bottom-Up
A in MTEP19 | B>A | East | WPSC | 16345 | 2022 Transmission Battery Bank Replacement project | Replace battery bank at transmission station. | MI | MI | Transmission stations have a battery bank that provides a direct current source for the protective relaying apparatus and protection equipment trip schemes. Poor tests may result from routine testing throughout the year, including the buildup of sediment in cells, high internal resistance, or visual inspections revealing leaking or cracked post terminals. If a battery bank is tested, analyzed, and it is deemed that the bank has reached the end of its maintainable life cycle, replacement is the only option. Along with the installation of new battery banks, this project will include the addition of hydrogen detection safety systems at each location. | Other |  | Reliability | 2022-12-31 | 2022-12-31 | 69 | 0 | Y | 35000 | Bottom-Up
A in MTEP19 | B>A | West | XEL | 15735 | North Ironwood Sub | Install new 115kV breaker and 115kV feeder into new Penokee Range Substation near existing Ironwood | MI | MI | Existing 4kV substation equipment is at end of life. New site across street is capable of supporting larger distribution substation footprint. | Other |  | Age and Condition | 2020-10-15 | 2020-10-15 | 115 | 12.5 | Y | 400000 | Bottom-Up
B in MTEP20 | B | West | ATC | 18018 | Forsyth - Gwinn, 69kV, new line | New 69kV transmission line. | MI | MI | Reliability - Operational Flexibility |  |  |  | 2023-12-31 | 2023-12-31 | 69 | 0 | Y | 4000000 | Bottom-Up
B in MTEP20 | B | West | ATC | 18049 | 9 mile SW STA – Portage (6901/6902), 69kV, Re-insulate | 9 mile SW STA – Portage (6901/6902), 69kV, Re-insulate | MI | MI | Asset Renewal - Re-insulation |  |  |  | 2023-12-31 | 2023-12-31 | 69 | 0 | Y | 3000000 | Bottom-Up
B in MTEP20 | B | East | ITCT | 18206 | Pioneer 120 kV Capacitor | Install a 54 MVAR capacitor at Pioneer 120 kV bus 101. | MI | MI | MISO identified low voltage issue at Pioneer and State buses under P6 contingencies in their initial MTEP19 study models. |  |  |  | 2024-06-01 | 2024-06-01 | 120 | 0 | Y |  | Bottom-Up
B in MTEP20 | B | East | ITCT | 18207 | Riverview – Tandem 120 kV Rebuild | Rebuild approximately 2.75 miles of 795 & 954 ACSR to 1431 ACSR and upgrade station equipment at Tandem. | MI | MI | MISO identified thermal issues on the Riverview - Tandem 120 kV line for P2 contingencies in their initial MTEP19 study models. |  |  |  | 2024-06-01 | 2024-06-01 | 120 | 0 | Y |  | Bottom-Up
B in MTEP20 | B | East | ITCT | 18208 | Airport - WDHVN Tap 120 kV Sag Remediation | Raise the sag on Airport - WDHVN Tap 120 kV section up to the conductor's limit. | MI | MI | MISO identified thermal issues on the Airport - WDHVN Tap 120 kV section for P6 contingencies in their initial MTEP19 study models. |  |  |  | 2024-06-01 | 2024-06-01 | 120 | 0 | Y |  | Bottom-Up
B in MTEP19 | B | West | ATC | 16488 | Tilden SS - Control House Replacement and Breaker & Relay Asset Renewal | Asset Renewal of Circuit Breakers, Switches, PT's, Relays, and install New Control Building | MI | MI | Asset Renewal - Substation | Other |  | Age and Condition | 2025-12-01 | 2025-12-01 | 138 | 138 | Y | 5484000 | Bottom-Up
B in MTEP19 | B | West | ATC | 16489 | Empire SS - Control House Replacement and Breaker & Relay Asset Renewal | Asset renewal of circuit breakers, PT's, relays, switches and install new control building | MI | MI | Asset Renewal - Substation | Other |  | Age and Condition | 2025-12-01 | 2025-12-01 | 138 | 138 | Y | 6732000 | Bottom-Up
B in MTEP19 | B | East | ITCT | 3143 | Northwest - Southfield 120 kV | Rebuild approximately 0.13 mile of 477 ACSR conductor on the Northwest – CTL17-2 120 kV section to 1431 ACSR to match the rest of the overhead conductor on this Northwest – Southfield 120 kV circuit. Also, upgrade the station equipment at Northwest 120 kV. | MI | MI | The 120 kV overhead section from Northwest to CTL17-2 junction (Northwest – Southfield 120 kV) is projected to overload for a couple shutdown-plus-contingency that involve the loss of Belle River – St. Clair 345 kV or Drake – Quaker 120 kV lines. The overloaded facilities are the 477 ACSR conductor and station equipment at Northwest. | BRP |  |  | 2029-12-31 | 2029-12-31 | 120 | 0 | Y | 172000 | Bottom-Up
B in MTEP19 | B | East | ITCT | 15751 | Fitz 345/120 kV Transformer #2 | The proposed solution is to install a second 345/120 kV transformer at Fitz. It should have design specs that are similar to the recently installed Transformer #1, and its summer emergency rating should be no less than 750 MVA/3608 Amps. | MI | MI | Transformer #1 at Fitz is projected to become overloaded for the shutdown plus contingency scenario involving the Belle River – Lenox 345 kV and Belle River – St. Clair 345 kV lines. The overloads were identified in the 2023 near-term peak load and 2028 long-term peak and off-peak load models with the Ludington units generating with flow to IESO across the Michigan-Ontario interface. | BRP |  |  | 2027-12-31 | 2027-12-31 | 345 | 120 | Y | 7300000 | Bottom-Up
B in MTEP19 | B | East | ITCT | 15842 | Bennett - Greenwood 120 kV Sag Remediation | Remediate the sag limit on the entire ~29.9 mile-long length of 954 ACSR conductor of the Bennett – Greenwood 120 kV line to at least the planned target summer normal/summer emergency rating of 170 MVA/816 Amps. | MI | MI | The Bennett – Greenwood 120 kV line is projected to become overloaded for shutdown plus contingency scenarios involving the Greenwood – Kilgore 120 kV line and Greenwood 345/120 kV Transformer #1. The overloads were identified in the 2020 and 2023 near-term 70% peak load models with the Ludington units pumping regardless of the flow across the Michigan-Ontario interface. | BRP |  |  | 2028-12-31 | 2028-12-31 | 120 | 0 | Y | 600000 | Bottom-Up
B in MTEP19 | B | East | ITCT | 15843 | Lee – Lake Huron Pumping 1 Tap 120 kV Rebuild | The proposed solution is to rebuild ~5.4 miles of the Lee – Lake Huron Pumping 1 Tap 120 kV section of the Lee – Menlo 120 kV line that is comprised of 266 ACSR conductor only utilizing 954 ACSR conductor and upgrade the 266 ACSR line entrance at Lee. | MI | MI | The Lee – Lake Huron Pumping 1 Tap 120 kV section of the Lee – Menlo 120 kV line is projected to become marginally overloaded in the five year out models for shutdown plus contingencies involving either the Belle River – St. Clair 345 kV line. This line is significantly overloaded in the 10 year out models. The overloads were identified peak and off-peak load models with the Ludington units generating and flow out of ITCT across the Michigan-Ontario interface. | BRP |  |  | 2027-12-31 | 2027-12-31 | 120 | 0 | Y | 2600000 | Bottom-Up
B in MTEP19 | B | East | ITCT | 15844 | Burns 2 Tap – Fitz 120 kV Sag Remediation | The proposed solution is to remediate the sag limit on the Burns 2 Tap – Fitz 120 kV section of the Adams – Fitz 120 kV line to increase its summer emergency rating to a minimum of 377 MVA/1814 Amps. The in-service date of the proposed project is December 31, 2022. | MI | MI | The Burns 2 Tap – Fitz 120 kV section of the Adams – Fitz 120 kV line is projected to become overloaded for shutdown plus contingency scenarios involving the Belle River – St. Clair 345 kV line plus either Belle River – Lenox 345 kV or the Bunce Creek – Fitz 120 kV line. The overloads were identified in the 2023 and 2028 peak load models with either flow to IESO or zero flow across the Michigan-Ontario interface while the Ludington units are generating. | BRP |  |  | 2028-12-31 | 2028-12-31 | 120 | 0 | Y | 198000 | Bottom-Up
B in MTEP19 | B | East | ITCT | 15846 | Lee Capacitor | The proposed solution is to install an 18 MVAR capacitor at Lee station to maintain acceptable voltage levels within this region of the Thumb area. | MI | MI | Low voltage is projected to occur at the Carrigan 120 kV, Lake Huron Pumping 1 120 kV, and Lake Huron Pumping 1 Tap 120 kV buses for shutdown plus contingency scenarios involving either the Carrigan – Wabash 120 kV line or the DTE Wabash 120/40 kV Transformer #102 plus either the Greenwood – Kilgore 120 kV or the Micah – Kilgore 120 kV line. The low voltage violations were identified in the 2020, 2023, and 2028 peak and off-peak load models with the Ludington units generating and were most prevalent when flow was to IESO across the Michigan-Ontario interface. | BRP |  |  | 2028-12-31 | 2028-12-31 | 120 | 0 | Y | 900000 | Bottom-Up
B in MTEP19 | B | East | ITCT | 15861 | Bunce Creek – Fitz 120 kV Rebuild | The proposed solution is to rebuild ~12.5 miles of the Bunce Creek – Fitz 120 kV line that is comprised of 795 ACSR and six-wired 477 ACSR conductor only utilizing 2156 ACSS conductor and reterminate the line from Bus 101 to Bus 104 at Bunce Creek. | MI | MI | The Bunce Creek – Fitz 120 kV line is projected to become overloaded for numerous contingency types with the most severe loadings caused by shutdown plus contingencies involving the Belle River – St. Clair 345 kV line plus one of a number of other transmission facilities. The overloads were identified in the 2023 and 2028 peak load models with the Ludington units generating and the flow is mainly to IESO across the Michigan-Ontario interface. In addition, low voltage is projected to occur at the Bunce Creek, Carrigan, Lake Huron Pumping, Menlo, Wabash, and Yuma 120 kV buses for the shutdown plus contingency scenario involving the Axle – St. Clair 120 kV line and Bunce Creek SB 101-102. These voltage violations were identified in the 2023 and 2028 peak load models when the Ludington units are generating regardless of the directional flow along the Michigan-Ontario interface. | BRP |  |  | 2027-12-31 | 2027-12-31 | 120 | 0 | Y | 18676000 | Bottom-Up
B in MTEP19 | B | East | ITCT | 15867 | Brownstown – Elm #2 230 kV Rebuild | Rebuild approximately 10.9 miles of 1431 ACSR conductor to 2156 ACSR on the Brownstown – Elm #2 230 kV circuit. Also, upgrade the station equipment at both ends. | MI | MI | The Brownstown – Elm #2 230 kV circuit is projected to overload for shutdown-plus-contingency that takes out Brownstown – Fermi #2 345 kV and Brownstown-Wayne #2 345 kV lines. The limiting elements on this circuit are the 1431 ACSR conductor and station equipment at both stations. | BRP |  |  | 2028-12-31 | 2028-12-31 | 230 | 0 | Y | 15766000 | Bottom-Up
B in MTEP19 | B | East | ITCT | 15870 | Brownstown 120 kV – Upgrade JA Station Equipment | Upgrade the station equipment at Brownstown 120 kV position “JA”. | MI | MI | The 345/120kV transformer #304 at Brownstown projected to be close to overload for a shutdown-plus-contingency event that takes out Brownstown – Fermi 345 kV and Brownstown – Wayne 345 kV lines. The limiting element on this transformer branch is the station equipment at Brownstown position “JA”. | BRP |  |  | 2025-12-31 | 2025-12-31 | 120 | 0 | Y | 20000 | Bottom-Up
B in MTEP19 | B | East | ITCT | 15871 | Brownstown-Monroe #1 345 kV Rebuild | Rebuild the 2-954 ACSR section (approximately 7.3 miles) of the Brownstown-Monroe #1 345 kV circuit to 2-1431 ACSR. Also, raise the sag on the 2-1431 ACSR section to at least 2061 MVA and upgrade station equipment at both Brownstown and Monroe 345 kV stations. | MI | MI | The Brownstown – Monroe 345 kV circuit is projected to be heavily overloaded for G-1, T-1, and many other contingencies that take out the Monroe – Wayne #1 345 kV line. The identified overloaded facilities are the 2-954 ACSR conductor, sag limits, and equipment at Brownstown and Monroe 345 kV stations. | BRP |  |  | 2028-12-31 | 2028-12-31 | 345 | 0 | Y | 18916000 | Bottom-Up
B in MTEP19 | B | East | ITCT | 15872 | Brownstown-Monroe #2 345 kV Sag Remediation | Raise the sag limit on Brownstown – Monroe #2 345 kV line to at least 1361 MVA. | MI | MI | The Brownstown – Monroe #2 345 kV circuit is projected to be marginally overloaded for a shutdown-plus-contingency that takes out Monroe – Coventry 345 kV and Milan-Monroe-Morocco 345 kV lines. The identified overloaded equipment on this circuit is the sag limit. The thermal violation only occurs at peak in the 5 and 10 year cases. | BRP |  |  | 2028-12-31 | 2028-12-31 | 345 | 0 | Y | 650000 | Bottom-Up
B in MTEP19 | B | East | ITCT | 15873 | Brownstown - Wayne #2 345 kV Station Equipment Upgrade | Upgrade the station equipment at Brownstown 345 kV positions “FM” and “FT”. | MI | MI | The Brownstown – Wayne #2 345 kV circuit is projected to be marginally overloaded for a shutdown-plus-contingency that takes out Brownstown – Fermi #2 345 kV and Monroe – Wayne #1 345 kV lines. The overloaded facility is the station equipment at Brownstown 345 kV positions “FM” and “FT”. | BRP |  |  | 2026-12-31 | 2026-12-31 | 345 | 0 | Y | 560000 | Bottom-Up
B in MTEP19 | B | East | ITCT | 15874 | Custer 120 kV – Upgrade GA Station Equipment | Upgrade the station equipment at Custer 120 kV position “GA”. | MI | MI | The 120 kV bus-tie between bus 102 and 103 at Custer is projected to marginally overload for a shutdown-plus-contingency or double-circuit tower outage that takes out the Monroe – Lallendorf 345 kV and Morocco-Milan-Monroe 345 kV lines. The limiting element on this 120 kV bus-tie branch is the station equipment at Custer position “GA”. | BRP |  |  | 2027-12-31 | 2027-12-31 | 120 | 0 | Y | 90000 | Bottom-Up
B in MTEP19 | B | East | ITCT | 15875 | Kentucky - Luzon 120 kV Sag Remediation | Completely remove the sag limit on the Kentucky – Luzon 120 kV line. | MI | MI | The Kentucky – Luzon 120 kV line is projected to be overloaded for several shutdown-plus-contingency that involve the loss of the Brownstown – Swan Creek 120 kV line. The identified overloaded equipment on this circuit is the sag limit. The thermal violations are found on all cases in the 2018 assessment. | BRP |  |  | 2028-12-31 | 2028-12-31 | 120 | 0 | Y | 500000 | Bottom-Up
B in MTEP19 | B | East | ITCT | 15917 | Fermi 345kV SVC | Install a -50/+250 MVAR SVC near the Fermi 345kV switchyard. The SVC will be installed at a new switchyard outside Fermi property, tentatively named Leroux. One 345kV circuit (length TBD based on station siting, but approximately 2 miles in total) will be installed on the vacant side of either Fermi-Brownstown #2 or Fermi-Brownstown #3 345kV structures from the new station into the existing Fermi switchyard. | MI | MI | The 2018 Fermi 2 Nuclear Plant NPOA Transmission study demonstrated an inability of the system to adhere to ITC's transient voltage recovery criteria for all tested contingencies. In addition, voltages lower than the bus specific criteria at the Fermi 345kV bus (<0.984 pu) were identified in an ongoing MISO attachment Y study. This project is being proposed by ITC as a mitigation for that constraint. | BRP |  |  | 2022-06-01 | 2022-06-01 | 345 | 0 | Y | 40000000 | Bottom-Up
B in MTEP19 | B | East | ITCT | 15923 | SVC for Import at Fermi | Increase the total SVC capability of the Fermi 345kV SVC project (MTEP #15917) by 300 MVAR (for a total of +900 MVAR) for import capability into the LP of Michigan. Each SVC at Fermi would be a -50/+450 MVAR range SVC. The additional 300 MVAR would be all Mechanically Switched Capacitor Banks, controlled by the SVC controls. | MI | MI | Import capability into the LP of Michigan. | Other |  | Reliability | 2023-06-01 | 2023-06-01 | 345 | 0 | Y | 2000000 | Bottom-Up
B in MTEP19 | B | East | ITCT | 15954 | Evergreen 120 kV – Upgrade HG Station Equipment | Upgrade the station equipment at Evergreen 120 kV position “HG”. | MI | MI | The 120 kV bus-tie between bus 101 and 102 at Evergreen is projected to marginally overload for a shutdown-plus-contingency event that takes Evergreen – Warren 120 kV and Hines – Wayne 230 kV lines. The limiting element on this 120 kV bus-tie branch is the station equipment at Evergreen position “HG”. | BRP |  |  | 2026-12-31 | 2026-12-31 | 120 | 0 | Y | 75000 | Bottom-Up
B in MTEP19 | B | East | ITCT | 15963 | Quaker-Drexel Tap 120 kV Rebuild | Rebuild approximately 2.6 miles of 954 ACSR conductor on the Quaker – Drexel 120 kV section to 2156 ACSR. Also, upgrade the station equipment at Quaker 120 kV. | MI | MI | The 120 kV section from Quaker to Drexel Tap (Quaker – Southfield 120 kV) is projected to overload for a couple shutdown-plus-contingency that involve the loss of Quaker – Sunset 120 kV line. The overloaded facilities are the 954 ACSR conductor and station equipment at Quaker. | BRP |  |  | 2028-12-31 | 2028-12-31 | 120 | 0 | Y | 2725000 | Bottom-Up
B in MTEP19 | B | East | ITCT | 15986 | Remer 120 kV Breakers | Install three new breakers at the Remer 120 kV station to tie buses 101 and 102 together and to terminate Remer to St. Clair circuits 1 & 2 at positions “HD” and “HI” respectively. | MI | MI | The Remer 120 kV station currently does not have a section breaker connecting buses 101 and 102 together or line breakers on Remer to St. Clair circuits 1 & 2. The two Remer 120 kV buses are connected on the 40 kV sub-transmission via a 120/40 kV transformer at each bus. When either the St. Clair breaker “HO” or St. Clair breaker “KG” is opened, flow from the Dean generation is forced down one of the Remer transformers, across the 40 kV system, then back up the other Remer transformer resulting in dynamic instability in the area. The transformers themselves are also exposed to potential overloads as the full capacity of the Dean generation exceeds the rating of each 120/40 kV transformer. | Other |  | Reliability | 2021-12-31 | 2021-12-31 | 120 | 0 | Y | 1200000 | Bottom-Up
B in MTEP19 | B | East | ITCT | 16007 | Pontiac 120 kV – Upgrade HC & GQ Station Equipment | Upgrade the station equipment at Pontiac 120 kV positions “HC” and “GQ”. | MI | MI | The 345/120kV transformers #301 and #303 at Pontiac are projected to be marginally overloaded for a shutdown-plus-contingency that takes out one of them plus the Bloomfield – Pontiac 230 kV line. The limiting element on these transformer branches are station equipment at Pontiac 120 kV positions “HC” and “GQ”. | BRP |  |  | 2027-12-31 | 2027-12-31 | 120 | 0 | Y | 40000 | Bottom-Up
B in MTEP19 | B | East | ITCT | 16010 | Chestnut – Logan 1 Tap 120 kV Sag Remediation | Raise the sag limit on the Chestnut – Logan 1 tap 120 kV section to at least 250 MVA. | MI | MI | The 120 kV section between Chestnut and Logan 1 tap is projected to marginally overload for a couple shutdown-plus-contingency that take out the Northeast – Skylark 120 kV line. The limiting element on this circuit is sag limit. | BRP |  |  | 2027-12-31 | 2027-12-31 | 120 | 0 | Y | 612000 | Bottom-Up
B in MTEP19 | B | East | ITCT | 16011 | Lenox 2nd 345/120 kV Transformer | Install a second 345/120 kV transformer at Lenox to offload the existing transformer #301. | MI | MI | The 345/120kV transformer #301 at Lenox is projected to overload for a shutdown-plus-contingency that takes out the Belle River – St. Clair 345 kV and Jewell – Lenox 345 kV lines. The limiting element on this branch is the transformer, breaker and station equipment at Lenox 120 kV position “HD”. | BRP |  |  | 2028-12-31 | 2028-12-31 | 345 | 120 | Y | 8400000 | Bottom-Up
B in MTEP19 | B | East | ITCT | 16012 | Golf 120 kV 54 MVAR Capacitor | The proposed solution is to install a 54 MVAR capacitor at Golf station to maintain acceptable voltage levels within this region of the Oakland area. | MI | MI | Low voltage is projected to occur at the Golf 120 kV, Houston 120 kV, and Macomb 120 kV buses for shutdown plus contingency scenarios involving a DTE transformer in surround area plus either the Macomb – Staphens 120 kV line or the Golf – Bismarck 120 kV line. The low voltage violations were identified in the 2020, 2023, and 2028 peak and off-peak load models. | BRP |  |  | 2022-12-31 | 2022-12-31 | 120 | 0 | Y | 1030000 | Bottom-Up
B in MTEP19 | B | East | ITCT | 16016 | Pontiac - Joslyn 120 kV Rebuild | The proposed solution is to rebuild 0.797 mile of the Pontiac – Joslyn 120kV circuit using 2156 ACSR conductor with single circuit steel structures and replace terminal equipment at Joslyn Pos HI. | MI | MI | The Pontiac – Joslyn 120kV line is projected to overload for various contingency scenarios, the worst is a breaker fault on the Pontiac circuit breaker JB or GZ. The identified overloaded equipment on this circuit are the conductor and terminal equipment at Joslyn Pos HI. The thermal violations are found on peak cases. | BRP |  |  | 2028-12-31 | 2028-12-31 | 120 | 0 | Y | 2506000 | Bottom-Up
B in MTEP19 | B | East | ITCT | 16017 | Jewell – St. Clair #1 345 kV Rebuild | Rebuild approximately 30.2 miles of the Jewell – St. Clair #1 345 kV line to 2-2156 ACSR. Also, upgrade station equipment at Jewell and St. Clair 345 kV stations. | MI | MI | The Jewell – St. Clair 345 kV circuit is projected to overload for several shutdown-plus-contingency and double-circuit tower contingencies that involve the loss of St. Clair – Stephens #2 345 kV and or Belle River – Lenox 345 kV lines. The overloaded facilities are the 2-954 ACSR conductor, sag limit, and equipment at Jewell and St. Clair 345 kV stations. | BRP |  |  | 2027-12-31 | 2027-12-31 | 345 | 0 | Y | 77800000 | Bottom-Up
B in MTEP19 | B | East | ITCT | 16018 | Jewell – Lenox 345 kV Rebuild | Rebuild approximately 8.3 miles of the Jewell – Lenox 345 kV line to 2-1431 ACSR. Also, upgrade station equipment at Jewell and Lenox 345 kV stations. | MI | MI | The Jewell – Lenox 345 kV circuit is projected to overload for numerous contingencies, including a T-1 that takes out Belle River – St. Clair 345 kV line. The overloaded facilities are the 2-954 ACSR conductor, sag limit, and equipment at Jewell and Lenox 345 kV stations. | BRP |  |  | 2029-12-31 | 2029-12-31 | 345 | 0 | Y | 20031000 | Bottom-Up
B in MTEP19 | B | East | ITCT | 16019 | Belle River – Lenox 345 kV Rebuild | Rebuild approximately 19.6 miles of the Belle River – Lenox 345 kV line to 2-T2 795 ACSR. Also, upgrade station equipment at Belle River 345 kV. | MI | MI | The Belle River – Lenox 345 kV circuit is projected to overload for numerous contingencies, including a T-1 that takes out Belle River – St. Clair 345 kV line. The overloaded facilities are the 2-954 ACSR conductor, sag limit, and station equipment at Belle River 345 kV.. | BRP |  |  | 2029-12-31 | 2029-12-31 | 345 | 0 | Y | 55460000 | Bottom-Up
B in MTEP19 | B | East | ITCT | 16021 | Belle River – St. Clair 345 kV Rebuild | Rebuild approximately 1.13 miles of the Belle River – St. Claire 345 kV line using 2-T2 795 ACSR conductor. Also, upgrade station equipment at Belle River and St. Clair 345 kV stations. The 2-T2 795 ACSR is the highest capacity conductor in the ITCT footprint at the time of this project and is presumed to be used for this 345 kV rebuild. Final conductor type chosen for this project pending Engineering & Design’s input. | MI | MI | The Belle River – St. Claire 345 kV circuit is projected to be heavily overloaded for numerous contingencies, including basecase, G-1, and T-1 contingencies. The overloaded facilities are all the conductors on this circuit and most of the station equipment at Belle River 345 kV and St. Claire 345 kV stations, including 345 kV breakers. | BRP |  |  | 2028-12-31 | 2028-12-31 | 345 | 0 | Y | 9300000 | Bottom-Up
B in MTEP19 | B | East | ITCT | 16024 | River Rouge 120 kV Capacitor | Install a three 18 MVAR capacitors at River Rouge 120 kV station. | MI | MI | There are numerous voltage issues in the region near River Rouge, Riverview, and Trenton Channel 120 kV stations. The main driving contingency for these voltage violations is the loss of the Navarre 230/120kV transformer and or the Brownstown 345/120kV transformer #301. | BRP |  |  | 2021-12-31 | 2021-12-31 | 120 | 0 | Y | 1030000 | Bottom-Up
B in MTEP19 | B | East | ITCT | 16066 | Pontiac – Colorado Tap 120 kV Rebuild | Rebuild approximately 1.9 miles of 954 ACSR conductor to 1431 ACSR on the Pontiac – Colorado tap (toward Sunbird) 120 kV section and upgrade station equipment at Pontiac 120 kV. | MI | MI | The 120 kV section between Pontiac and Colorado tap on the Pontiac – Sunbird 120 kV circuit is projected to overload a shutdown-plus-contingency that takes out Pontiac – Joslyn 120 kV and Pontiac – Walton 120 kV lines. The overloaded facilities are the 954 ACSR conductor and station equipment at Pontiac 120 kV. | BRP |  |  | 2028-12-31 | 2028-12-31 | 120 | 0 | Y | 2533000 | Bottom-Up
B in MTEP19 | B | East | ITCT | 16068 | Benson – Stephens 120 kV Rebuild | Rebuild approximately 1.17 miles of 795 ACSR conductor to 1431 ACSR on the Benson – Stephens 120 kV section and upgrade station equipment at Stephens 120 kV. | MI | MI | The 120 kV section Benson tap to Stephens is projected to overload a shutdown-plus-contingency that takes out Bismarck – Golf 120 kV and Victor – Lenox 120 kV lines. The overloaded facilities are the 795 ACSR conductor, sag limit, and station equipment at Stephens 120 kV. | BRP |  |  | 2028-12-31 | 2028-12-31 | 120 | 0 | Y | 1614000 | Bottom-Up
B in MTEP19 | B | East | ITCT | 17631 | Mack - Northeast 120 kV Reconductor and Station Work | Reconductor approximately 6.5 miles of the Northeast – Mack cable utilizing 230 kV 3500 Kcmil cable. Un-parallel the Northeast reactors by removing breaker GB and replace reactor HC with a new 5% 400 MVA SE reactor (replacing reactor KD with existing reactor HC). | MI | MI | Un-paralleling the Northeast reactors and re-cabling the Mack – Northeast 120 kV circuit mitigates the following overloads and future projects; • Underground cable rebuild portion and 3.5 miles of overhead rebuild of MTEP19 project #16023 (Lincoln-Northeast-Northwest 120 kV Rebuild) • Mitigates a base case marginal overload (~98% SN) on the Northeast end of the Lincoln-Northeast-Northwest 120 kV circuit • Mitigates marginal overloads (~99% SE) on the overhead portion of the Northeast – Hilton Road 120 kV circuit • Mitigates a marginal overload (~99% SE) on the Cato – Waterman 120 kV circuit | BRP |  |  | 2023-06-01 | 2023-06-01 | 120 | 0 | Y | 47000000 | Bottom-Up
B in MTEP19 | B | East | METC | 9881 | Claremont - Manning #2 138 kV Sag Remediation | The proposed solution is to remediate the sag limit on the Claremont – Manning 2 138 kV line and upgrade terminal equipment at Claremont to increase the summer emergency rating to a minimum of 330 MVA/1382 Amps. | MI | MI | The Claremont – Manning 2 138 kV line is projected to become overloaded for shutdown plus contingency scenarios involving either the Claremont – Manning 1 138 kV, Claremont – Portsmouth Tap 138 kV, or the Manning – Portsmouth Tap 138 kV facilities plus another transmission facility. The overloads were identified in the 2020, 2023, and 2028 peak and off-peak load models and are the most severe with the Ludington units generating and flow to ITCT across the Michigan-Ontario interface. | BRP |  |  | 2022-12-31 | 2022-12-31 | 138 | 0 | Y | 1364000 | Bottom-Up
B in MTEP19 | B | East | METC | 15752 | Redstone – Tittabawassee 138 kV Rebuild | The proposed solution is to rebuild ~13.4 miles of the Redstone – Tittabawassee 138 kV line that is comprised of 336 ACSR conductor only utilizing 1431 ACSR conductor and upgrade the 336 ACSR line entrance at Redstone. | MI | MI | The Redstone – Tittabawassee 138 kV line is projected to become overloaded for numerous contingency types with the most severe loadings caused by shutdown plus contingencies involving either the Redstone – Regal 138 kV, Bluegrass Tap – Luce 138 kV, or the Bluegrass Tap – Summerton 138 kV facility plus one of a number of other transmission facilities. The overloads were identified in the 2020, 2023, and 2028 peak and off-peak load models regardless of the status of the Ludington units or the flow across the Michigan-Ontario interface. | BRP |  |  | 2022-12-31 | 2022-12-31 | 138 | 0 | Y | 17800000 | Bottom-Up
B in MTEP19 | B | East | METC | 15758 | Luce – Summerton 138 kV Reconductor | The proposed solution is to reconductor ~10.5 miles of the Luce – Summerton 138 kV line that is comprised of 336 ACSR conductor only utilizing 954 ACSR conductor. | MI | MI | The Luce – Summerton 138 kV line is projected to become overloaded for numerous contingency types with the most severe loadings caused by shutdown plus contingencies involving the Redstone – Tittabawassee 138 kV line plus one of a number of other transmission facilities. The overloads were identified in the 2020, 2023, and 2028 peak and off-peak load models with the majority occurring when the Ludington units are pumping and flow is to IESO across the Michigan-Ontario interface. | BRP |  |  | 2026-12-31 | 2026-12-31 | 138 | 0 | Y | 5000000 | Bottom-Up
B in MTEP19 | B | East | METC | 15789 | Livingston - McGulpin 138 kV Line | The proposed solution is to rebuild ~30.4 miles of the Riggsville – Vanderbilt 138 kV portion of the ~40.1 mile-long Livingston – Riggsville 138 kV line and the entire ~19.5 mile-long McGulpin – Riggsville 138 kV line, which are both comprised of 266 ACSR conductor only utilizing 954 ACSR conductor on 230 kV double-circuit structures. Install 954 ACSR conductor on the other side of these structures to construct the new ~59.6 mile-long Livingston – McGulpin 138 kV line. | MI | MI | The following facilities are projected to become overloaded for numerous shutdown plus contingency scenarios, the majority of which involve outages of transmission facilities along two of the three 138 kV transmission paths north of Livingston station in the northern lower peninsula of Michigan: • Riggsville – Vanderbilt 138 kV portion of Livingston – Riggsville 138 kV • Alpena – Rockport 138 kV • Emmet – Livingston 138 kV • Emmet – Oden 138 kV • McGulpin – Riggsville 138 kV The overloads were identified in the 2020, 2023, and 2028 peak and off-peak load models and were most severe with south to north flow (51 MW) across the ATC HVDC device, the Ludington units generating, and flow to ITCT across the Michigan-Ontario interface. | BRP |  |  | 2026-06-01 | 2026-06-01 | 138 | 0 | Y | 66552000 | Bottom-Up
B in MTEP19 | B | East | METC | 15795 | Gallagher - Greenwood Tap 138 kV Sag Remediation | The proposed solution is to remediate the sag limit on the Gallagher – Greenwood Tap 138 kV section of the Bard Road – Gallagher 138 kV line to increase its summer emergency rating to a minimum of 165 MVA/691 Amps. | MI | MI | The Greenwood Tap 138 kV section of the Bard Road – Gallagher 138 kV line is projected to become overloaded for shutdown plus contingency scenarios involving either the Bullock – Warren 138 kV or Bullock – Edenville Tap 138 kV facility plus either the Higgins - Mio 138 kV, Mio – Ryno Tap 138 kV, or Higgins – Ryno Tap 138 kV facility. The overloads were identified in the 2020, 2023, and 2028 peak load models with the Ludington units generating regardless of the directional across the Michigan-Ontario interface. | BRP |  |  | 2021-12-31 | 2021-12-31 | 138 | 0 | Y | 675000 | Bottom-Up
B in MTEP19 | B | East | METC | 15796 | Dort - Thetford 2 138 kV Rebuild | The proposed solution is to rebuild ~1.6 miles of the Dort – Thetford 2 138 kV line that is comprised of 795 ACSR conductor utilizing 1431 ACSR conductor and upgrade the 795 ACSR line entrance at Dort. | MI | MI | The Dort – Thetford 2 138 kV line is projected to become overloaded for the shutdown plus contingency involving the Dort – Thetford 1 138 kV line plus Goss 345/138 kV Transformer #1. The overloads were identified in the 2020 peak load model with the Ludington units generating and flow is to ITCT across the Michigan-Ontario interface. | BRP |  |  | 2028-12-31 | 2028-12-31 | 138 | 0 | Y | 2153000 | Bottom-Up
B in MTEP19 | B | East | METC | 15799 | Claremont 138 kV Station Equipment Upgrades (Manning 1 Line) | The proposed solution is to upgrade station equipment at Claremont to increase the facility’s summer emergency rating to a minimum of 431 MVA/1805 Amps. | MI | MI | Station equipment at Claremont on the Portsmouth Tap 138 kV section of the Manning 1 138 kV line is projected to become overloaded for shutdown plus contingency scenarios involving the Karn – Saginaw River 138 kV and Claremont – Manning 2 138 kV lines. The overloads were identified in the 2020 and 2023 peak load models with the Ludington units generating and flow to ITCT across the Michigan-Ontario interface. | BRP |  |  | 2021-12-31 | 2021-12-31 | 138 | 0 | Y | 98000 | Bottom-Up
B in MTEP19 | B | East | METC | 15807 | Four Mile - Croton 138 kV Rebuild | The proposed solution is to rebuild 2.6 miles Algoma-Cedar Spring 138 kV section of the Four Mile-Croton circuit using 954 ACSR conductor. Pre-build it to 230kV construction to facilitate future 230kV expansion in the area. | MI | MI | Algoma Jct. – Cedar Spring Jct. section of the Croton – Four Mile 138kV line 138kV circuit is projected to overload fora shutdown plus contingency involving the Cobb – Felch Road and Tippy – Chase 138kV lines. The identified overloaded equipment on this circuit is the conductor. The thermal violations are only found on peak cases. | BRP |  |  | 2029-12-31 | 2029-12-31 | 138 | 0 | Y | 3744000 | Bottom-Up
B in MTEP19 | B | East | METC | 15809 | Four Mile - North Belding 138 kV Rebuild | The proposed solution is to rebuild 8.38 miles Alpine Jct. – Rogue River Jct. and Rogue River Jct. – Cannon Jct. sections of the Four Mile – North Belding 138kV line using 954 ACSR conductor. | MI | MI | Alpine Jct. – Rogue River Jct. and Rogue River Jct. – Cannon Jct. sections of the Four Mile – North Belding 138kV line are projected to overload for a shutdown plus contingency involving the North Belding – Vergenses and Marquette – Vergennes 138kV lines. The identified overloaded equipment on this circuit is the conductor. The thermal violations are only found on peak cases. | BRP |  |  | 2028-12-31 | 2028-12-31 | 138 | 0 | Y | 11700000 | Bottom-Up
B in MTEP19 | B | East | METC | 15810 | Roosevelt - Tallmadge 345 kV Rebuild | The proposed solution is to rebuild 16.41 miles of the Roosevelt-Tallmadge 345kV circuit using 2x1431 ACSR conductor with double circuit steel structures. Replace terminal equipment at Tallmadge and Roosevelt stations. Also replace station equipment at Tallmadge station. | MI | MI | The Roosevelt – Tallmadge 345kV line is projected to overload for a shutdown plus contingency involving the Campbell – Tallmadge and Gaines – Roosevelt 345kV lines. The identified overloaded equipment on this circuit is the conductor, terminal equipment at Tallmadge and Roosevelt, and station equipment at Tallmadge. The thermal violations are only found on off peak cases. | BRP |  |  | 2025-12-31 | 2025-12-31 | 345 | 0 | Y | 45900000 | Bottom-Up
B in MTEP19 | B | East | METC | 15811 | Tallmadge - Meyer 138 kV Rebuild | The proposed solution is to rebuild 1.08 miles of the Tallmadge – Meyer using 954 ACSR conductor with double circuit steel structures. | MI | MI | The Tallmadge – Meyer 138kV circuit is projected to overload for a shutdown plus contingency involving the Kenowa – Tallmadge and Meyer – Tallmadge 345kV lines. The identified overloaded equipment on this circuit is the conductor and sag. The thermal violations are only found on off peak cases. | BRP |  |  | 2025-12-31 | 2025-12-31 | 138 | 0 | Y | 650000 | Bottom-Up
B in MTEP19 | B | East | METC | 15812 | Tallmadge - Wealthy #1 138 kV Rebuild | The proposed solution is to rebuild 6.62 miles of the Tallmadge – Wealthy #1 138kV circuit using 2156 ACSR conductor with double circuit steel structures. Also replace station equipment at Tallmadge substation. | MI | MI | The Tallmadge – Wealthy #1 138kV circuit is projected to overload for the shutdown plus contingency involving the Four Mile – Tallmadge and Tallmadge – Wealthy #2 138kV lines. The identified overloaded equipment on this circuit is the conductor, sag, and terminal equipment and station equipment at Tallmadge and Wealthy stations. The thermal violations are only found on peak cases. | BRP |  |  | 2026-12-31 | 2026-12-31 | 138 | 0 | Y | 19700000 | Bottom-Up
B in MTEP19 | B | East | METC | 15813 | Tallmadge - Wealthy #2 138 kV Rebuild | The proposed solution is to rebuild 6.68 miles of the Tallmadge – Wealthy #2 138kV circuit using 2156 ACSR conductor with double circuit steel structures. Also replace station equipment at Tallmadge substation. | MI | MI | The Tallmadge – Wealthy #2 138kV circuit is projected to overload a shutdown plus contingency involving the Four Mile – Tallmadge and Tallmadge – Wealthy #1 138kV lines. The identified overloaded equipment on this circuit is the conductor, sag, and terminal equipment and station equipment at Tallmadge and Wealthy stations. The thermal violations are only found on peak cases. | BRP |  |  | 2027-12-31 | 2027-12-31 | 138 | 0 | Y | 10800000 | Bottom-Up
B in MTEP19 | B | East | METC | 15831 | Alma - Regal 2 138 kV Rebuild | Rebuild the entire ~5.8 mile-long Alma – Regal 2 138 kV line by replacing the existing assets (all structures, 336 ACSR conductor, and the 336 ACSR line entrance at Alma) with new structures that are designed for 954 ACSR conductor and install this conductor along with OPGW. | MI | MI | The Alma – Regal 2 138 kV line is projected to become overloaded for numerous contingency types with the most severe loadings caused by shutdown plus contingencies involving the Alma – Regal 1 138 kV line plus one of a number of other transmission facilities. The overloads were identified in the 2020, 2023, and 2028 70% peak load models with the Ludington units pumping and are more severe when the flow is to ITCT across the Michigan-Ontario interface. | BRP |  |  | 2029-12-31 | 2029-12-31 | 138 | 0 | Y | 5065000 | Bottom-Up
B in MTEP19 | B | East | METC | 15832 | Amber - Pere Marquette 138 kV Rebuild | Rebuild the entire ~1.3 mile-long Amber – Pere Marquette 138 kV line by replacing the existing assets (all structures, 336 ACSR conductor, 795 ACSR conductor, and the 795 ACSR line entrance at Pere Marquette) with new structures that are designed for 2156 ACSR conductor and install this conductor along with OPGW. METC will request that CE upgrade the limiting equipment at Position 188 at Amber. | MI | MI | The proposed solution is to rebuild the entire ~1.3 mile-long Amber – Pere Marquette 138 kV line that is comprised of 336 ACSR and 795 ACSR conductors utilizing 2156 ACSR conductor and upgrade the 795 ACSR line entrance at Pere Marquette. In addition, METC will request that CE upgrade the limiting equipment at Position 188 at Amber. | BRP |  |  | 2029-12-31 | 2029-12-31 | 138 | 0 | Y | 1753500 | Bottom-Up
B in MTEP19 | B | East | METC | 15837 | Chase - Mecosta 138 kV Rebuild | Rebuild ~7.2 miles of the Chase – Mecosta 138 kV line. Pre-build it to 230 kV construction to facilitate potential future 230 kV expansion in northern Michigan. Replace the existing assets (all structures, 110 copper conductor, 110 + 1/0 copper conductor) with new double-circuit structures that are designed for 954 ACSR conductor on each side and install this conductor along with OPGW for the existing line only. Also, remediate the sag limit on ~10.6 miles of 336 ACSR conductor to at least the planned target summer normal/summer emergency rating of 151 MVA/633 Amps. | MI | MI | The Chase – Mecosta 138 kV line is projected to become overloaded for shutdown plus contingencies involving either the Cobb – Felch Road 138 kV, Four Mile – Piston Ring Tap 138 kV, or the Croton – Felch Road 138 kV line and another transmission facility. The overloads were identified in the 2020, 2023, and 2028 peak and off-peak load models with the Ludington units generating regardless of the directional flow across the Michigan-Ontario interface. | BRP |  |  | 2029-12-31 | 2029-12-31 | 138 | 0 | Y | 10442500 | Bottom-Up
B in MTEP19 | B | East | METC | 15838 | Cheesman Tap - Regal 138 kV Rebuild | Rebuild the entire ~1.3 mile-long Cheesman Tap – Regal 138 kV portion of the ~7.8 mile-long Alma – Regal 1 138 kV line. Replace the existing assets (all structures, 336 ACSR conductor, and the 336 ACSR line entrance at Regal) with new structures that are designed for 954 ACSR conductor and install this conductor along with OPGW. | MI | MI | The Cheesman Tap – Regal 138 kV portion of the Alma – Regal 1 138 kV line is projected to become overloaded for shutdown plus contingencies involving the Alma – Regal 2 138 kV line and another transmission facility. The overloads were identified in the 2020 and 2023 70% peak load models with the Ludington units pumping and flow is to ITCT across the Michigan-Ontario interface. | BRP |  |  | 2029-12-31 | 2029-12-31 | 138 | 0 | Y | 1716000 | Bottom-Up
B in MTEP19 | B | East | METC | 15841 | Bullock - Summerton 138kV Rebuild | Rebuild the entire ~24.8 mile-long Bullock – Summerton 138 kV line by replacing the existing assets (all structures, 336 ACSR conductor, and the 336 ACSR line entrance at Bullock) with new structures that are designed for 954 ACSR conductor and install this conductor along with OPGW. | MI | MI | The Bullock – Summerton 138 kV line is projected to become overloaded for numerous contingency types involving the Redstone – Regal 138 kV line and another transmission facility. The overloads were identified in the 2020 and 2023 peak load models with the Ludington units generating and flow is to ITCT across the Michigan-Ontario interface. | BRP |  |  | 2028-12-31 | 2028-12-31 | 138 | 0 | Y | 32763000 | Bottom-Up
B in MTEP19 | B | East | METC | 15907 | Four Mile 138kV Station Equipment Upgrade | Replace station equipment at Four Mile station position 388. | MI | MI | Station equipment at Four Mile substation is projected to overload for a shutdown plus contingency involving the Gaines – Henry and Spaulding – Vergennes 138kV lines. The identified overloaded equipment on this circuit is station equipment. The thermal violations are found on peak cases. | BRP |  |  | 2028-12-31 | 2028-12-31 | 138 | 0 | Y | 50000 | Bottom-Up
B in MTEP19 | B | East | METC | 15910 | Marquette - Bingham 138 kV Rebuild | Rebuild 18.76 miles of the Marquette – Bingham circuit using 954 ACSR conductor with single circuit steel structures. | MI | MI | The David – Hubbardston Road and Hubbardston Road – Bingham sections of the Marquette – Bingham 138kV circuit are projected to become marginally overloaded for a shutdown plus contingency involving the Goss – Slate and Nelson Road – Murphy 345kV lines. The identified overloaded equipment on this circuit is the conductor. The thermal violation is only found on off peak cases. | BRP |  |  | 2027-12-31 | 2027-12-31 | 138 | 0 | Y | 22100000 | Bottom-Up
B in MTEP19 | B | East | METC | 15911 | Verona - Foundry 138kV Rebuild | Rebuild 16.1 miles of the Brewster Jct. – Convis Jct. and Convis Jct. – Calhoun sections of the Verona – Foundry 138 kV circuit using 954 ACSR conductor with future double-circuit (FDC) steel structures. | MI | MI | The Brewster Jct. – Convis Jct. section of the Verona – Foudry 138kV circuit is projected to marginally overload for a shutdown plus contingency involving the Argenta – Tompkin and Oneida – Battle Creek 345kV lines. The identified overloaded equipment on this circuit is the conductor. The thermal violations are found on off peak cases. | BRP |  |  | 2028-12-31 | 2028-12-31 | 138 | 0 | Y | 24300000 | Bottom-Up
B in MTEP19 | B | East | METC | 15937 | Marquette 138kV Station Equipment Upgrade | Replace the station equipment at Marquette substation Position 5070 | MI | MI | The Marquette – Lowell Jct. section of the Marquette – Vergennes 138kV circuit is projected to marginally overload for a shutdown plus contingency involving the North Belding – Vergennes and Four Mile – Alpine Jct. 138kV lines. The identified overloaded equipment on this circuit is station equipment. The thermal violations are found on peak cases. | BRP |  |  | 2028-12-31 | 2028-12-31 | 138 | 0 | Y | 80000 | Bottom-Up
B in MTEP19 | B | East | METC | 15993 | Keystone SVC | The proposed solution is to add +100/0 MVAR SVC (Static Var Compensator) and 100 MVAR MSC (Mechanical Switch Capacitor) at Keystone 120 kV 1. To provide the needed slow/fast reactive power supports to the bus voltages in Keystone 120 kV region, 2. To reduce the power flows on the Keystone 345/120 kV transformers. | MI | MI | Many bus voltages around Keystone 120 kV region in Area 218 METC are facing low voltage violations for shutdown plus contingency scenarios involving the Keystone - Livingston 345 kV line and the Keystone – Ludington 345 kV line. The low voltage violations were identified in the 2022 near-term peak load model. | BRP |  |  | 2023-12-31 | 2023-12-31 | 138 | 0 | Y | 20000000 | Bottom-Up
B in MTEP19 | B | East | WPSC | 15652 | Atlanta to Gaylord 138kV Rebuild | Rebuild 22 miles to Wolverine's 138 kV standard | MI | MI | Condition Based - Replace aging infrastructure. • Built in 1978, current age 40 years • 36 damaged poles • 15% of poles in need of replacement |  |  |  | 2021-12-31 | 2021-12-31 | 138 | 0 | Y | 11300000 | Bottom-Up
A in MTEP19 | B>A | West | XEL | 15743 | Hurley to Norrie Line | Construct a new 115kV line from Hurley to Norrie | MI,WI | MI,WI | Corrects low voltage conditions in the Ironwood area under N-1-1 contingency. | BRP |  |  | 2022-01-31 | 2022-01-31 | 115 | 0 | Y | 8000000 | Bottom-Up
A in MTEP20 | B>A | West | GRE | 14366 | Svea Tap - Litchfield Tap Line Rebuild Project | Rebuild GRE’s existing 69 kV transmission line from Willmar to Litchfield Muni Tap with a larger conductor. | MN | MN | GRE’s Willmar to Litchfield Muni Tap 69 kV line (DS line) is one of the oldest 69 kV transmission lines in the area. It is in need of a replacement due its age and condition. In addition, this transmission line provides support to a large load center at Litchfield Muni. System analysis shows the existing transmission system doesn’t have margin to serve new or growing loads in the Litchfield area within the required voltage criteria. In order to improve system voltage, and address reliability concerns due to the transmission line age and condition, GRE will rebuild the transmission line. Better system reliability and load serving performance will be gained in this area with 115 kV transmission line that extends between Willmar and Big Swan area. As a result, GRE will rebuild the DS line to 115 kV standard, but will continue to operate the line at 69 kV until the need to operate the transmission line at 115 kV is justifiable in the future. |  |  |  | 2024-06-14 | 2024-06-14 | 69 | 0 | Y | 18350000 | Bottom-Up
A in MTEP20 | B>A | West | GRE | 17664 | Portage Lake 115/69 kV Project | GRE will interconnect to Minnesota Power’s (MP) 13 Line (Riverton – Cromwell 115 kV) with a 4 position, 115 kV ring bus, to be called Portage Lake, at or near the existing Mille Lacs Electric Cooperative (MLEC) Kimberly substation. The new 115 kV Portage Lake ring bus will have four positions; 115 kV line to Riverton (13 Line), 115 kV line to Cromwell (26 Line), 115/69 kV transformer with a 9.5 mile line to Palisade. AKA Kimberly. | MN | MN | Reduce radial line exposure of the GRE Palisade, Big Sandy, Round Lake & Wright distribution substations. |  |  |  | 2023-06-01 | 2023-11-01 | 115 | 69 | Y | 12300000 | Bottom-Up
A in MTEP20 | B>A | West | GRE | 17944 | Heron Lake - Round Lake (FE-RH) 69 kV Line Rebuild | Rebuild entire FE-RH line (from Heron Lake substation to Round Lake substation) | MN | MN | Age & condition. The line was built in 1952. It is highly prone to galloping. The cost of mitigating galloping is nearly the cost of rebuilding. |  |  |  | 2021-04-01 | 2021-04-01 | 69 | 0 | Y | 13232725 | Bottom-Up
A in MTEP20 | B>A | West | GRE | 17964 | Blue Earth - East Chain - Wilbert Tap (FE-WB) 69 kV Line Rebuild | Rebuild entire FE-WB line (Blue Earth to East Chain to Wilbert Tap) | MN | MN | Reliability on the line has been poor and the line rebuild presents a better valued project versus mitigating the galloping without rebuild. |  |  |  | 2022-06-01 | 2022-06-01 | 69 | 0 | Y | 12273125 | Bottom-Up
A in MTEP20 | B>A | West | GRE | 17970 | Howard Lake - Highland - Maple Lake Line Rebuild | Rebuild the 69 kV transmission line from Howard Lake to Highland to Maple Lake. | MN | MN | Age and condition. |  |  |  | 2021-06-01 | 2021-06-01 | 69 | 0 | Y | 10402000 | Bottom-Up
A in MTEP20 | B>A | West | GRE | 17971 | Westwood 1 115 kV Conversion | Convert the existing GRE/SEA Westwood 1 substation from 69 kV to 115 kV service. Rebuild the existing 69 kV transmission line from Le Sauk to Westwood 1 to West St. Cloud to 115 kV. | MN | MN | Improve service reliability to Westwood 1, LeSauk and Five Point substations. |  |  |  | 2022-10-31 | 2022-10-31 | 115 | 0 | Y | 6020000 | Bottom-Up
A in MTEP20 | B>A | West | GRE | 17986 | Lake Jennie Tap 69 kV Line Rebuild | Rebuild 2.77 miles of Lake Jennie Tap line. | MN | MN | Age and condition. |  |  |  | 2023-06-01 | 2023-06-01 | 69 | 0 | Y | 1550000 | Bottom-Up
A in MTEP20 | B>A | West | GRE | 17988 | Lake Mary 115 kV Conversion | Convert the GRE/REA Lake Mary substation from 41.6 kV to 115 kV service. | MN | MN | The existing Lake Mary 41.6 kV substation is reaching capacity. |  |  |  | 2021-12-31 | 2021-12-31 | 115 | 0 | Y | 1400000 | Bottom-Up
A in MTEP20 | B>A | West | GRE | 18025 | Cannon River Park 115 kV Substation | Construct a new 115 kV transmission line from Cannon River Park to the Cannon River Park tap in the Xcel 0832 line near the Xcel Faribault Energy Park. | MN | MN | New load. |  |  |  | 2020-08-20 | 2020-08-20 | 115 | 0 | Y | 810000 | Bottom-Up
A in MTEP20 | B>A | West | ITCM | 17968 | Thisius 161/69kV Substation | ITCM will construct a 161:69kV substation at the crossing of the Huntley – Freeborn 161kV and Huntley – Walters 69kV circuits. | MN | MN | Low voltage on the 69kV system in the area and to increase operational flexibility in the Albert Lea area |  |  |  | 2027-12-31 | 2027-12-31 | 161 | 69 | Y |  | Bottom-Up
A in MTEP20 | B>A | West | ITCM | 18111 | J523 Generator Interconnection-TOIF | Install new terminal for J523 gen-tie line. This work includes installing switch, dead-end, CCVT's, switches, and relay panels (see GIA for further details). | MN | MN | TOIF required for the J523 Generator Interconnection | GIP |  |  | 2021-09-15 | 2021-09-15 | 161 | 161 | Y | 353826 | Externally Driven
A in MTEP20 | B>A | West | ITCM | 18113 | J523 Generator Interconnection Network Upgrades | Add two 161kV breakers in series with the bus-tie breaker 6620 to create a breaker and 1/2 row. Relocate the line for the Adams 345/161kV transformer from the existing terminal to a new terminal position on a breaker and 1/2 row (install dead end, coordinate relocation of metering with Xcel, and replace necessary equipment to accommodate the relocation of the transformer terminal). All new equipment must be capable of 2000 amp operation. | MN | MN | J523 Generator Interconnection Agreement required network upgrades | GIP |  |  | 2021-09-15 | 2021-09-15 | 161 | 161 | Y | 273780 | Externally Driven
A in MTEP20 | B>A | West | ITCM | 18114 | Adams 161kV Breaker and 1/2 Upgrade | Add a breaker to the 161kV bus between breakers 0681 and 0680 and relocate the Rochester and Harmony 161kV lines to terminal positions in the newly formed breaker and 1/2 row (install switches, bus work, dead-end, CCVTs, relays, and all necessary equipment as needed). Add a breaker to the 161kV bus between breakers 0685 and 0682 (install switches, bus work, dead-end, CCVTs, relays, and all necessary equipment as needed). Add a breaker to the 161kV bus between breakers 0790 and 0686 (install switches, bus work, dead-end, CCVTs, relays, and all necessary equipment as needed). All equipment needs to be capable of a minimum of 2000 amp operation. | MN | MN | The Adams 161kV conversion to breaker and 1/2 will address maintenance concerns at the substation and improve the operational flexibility of the 161kV system in the area. The breaker-and-1/2 upgrade will allow for a reduction in generation curtailment due to maintenance outages and 161 kV bus and breaker faults |  |  |  | 2021-09-15 | 2021-09-15 | 161 | 161 | Y |  | Bottom-Up
A in MTEP20 | B>A | West | MP | 15598 | Badoura Transformer Replacement | Replace existing 230/115 kV transformer at Badoura Substation. Add 230 kV line breakers and 115 kV transformer breaker. | MN | MN | Age & condition. Transformer is non-standard with an external voltage regulator (new transformer to include LTCs and be consistent with system spare). Project will also mitigate post-contingent overloads on the transformer and the Riverton - Pequot Lakes 115 kV Line following multiple-circuit events in the surrounding area | BRP |  |  | 2022-12-01 | 2022-12-31 | 230 | 115 | Y | 4500000 | Bottom-Up
A in MTEP20 | B>A | West | MP | 17870 | National Taconite Breaker Replacements | Replace existing breakers and associated equipment at National Taconite Substation | MN | MN | Age & condition |  |  |  | 2021-12-31 | 2021-12-31 | 115 | 0 | Y | 1300000 | Bottom-Up
A in MTEP20 | B>A | West | MP | 17871 | Laskin Breaker Replacements | Replace breakers and associated equipment at Laskin Substation | MN | MN | Age & condition |  |  |  | 2021-12-31 | 2022-12-31 | 115 | 0 | Y | 700000 | Bottom-Up
A in MTEP20 | B>A | West | MP | 18060 | 8 Line Relocation | Relocate & rebuild Fond Du Lac - Thomson 115 kV Line. Add a 115 kV breaker at Fond Du Lac. | MN | MN | Age & condition. Structures must be relocated off failing slope before they are compromised. Eliminate river crossings & enhance access & maintainability. Age & condition of existing line and conductor, better line and substation protection (breaker addition), and provides increased transmission line capacity. |  |  |  | 2022-12-31 | 2022-12-31 | 115 | 0 | Y | 3500000 | Bottom-Up
A in MTEP20 | B>A | West | MP | 18064 | Hibbing Breaker Replacements | Replace existing 115 kV circuit breakers and associated equipment at Hibbing Substation | MN | MN | Age & condition. Increased capability on Hibbing - 14 Line Tap and Hibbing - Virginia 115 kV lines. |  |  |  | 2022-12-31 | 2022-12-31 | 115 | 0 | Y | 1000000 | Bottom-Up
A in MTEP20 | B>A | West | MP | 18065 | Verndale Substation Modernization | Replace existing 115 kV circuit breakers at Verndale Substation | MN | MN | Age & condition |  |  |  | 2022-12-31 | 2022-12-31 | 115 | 0 | Y | 700000 | Bottom-Up
A in MTEP20 | B>A | West | MP | 18109 | 15th Ave West Transformer Addition | Add 115/34.5 kV transformer to existing 15th Ave West Substation. This project includes the transmission equipment necessary to accommodate the new transformer. | MN | MN | Redundancy and load-serving capability in downtown Duluth distribution system. |  |  |  | 2022-12-31 | 2022-12-31 | 115 | 34.5 | Y | 250000 | Bottom-Up
A in MTEP20 | B>A | West | MP | 18110 | Little Falls Bus Reconfiguration | Reconfigure Little Falls 115 kV bus to eliminate line-connected transformer configuration | MN | MN | Mitigates low voltages seen in study models at Little Falls, Blanchard, and Pepin Lake. Also provides better line & transformer protection. This is the transmission part of a large age & condition substation modernization project that also involves replacing the transformer and other distribution equipment. |  |  |  | 2022-12-31 | 2022-12-31 | 115 | 34 | Y | 250000 | Bottom-Up
A in MTEP20 | B>A | West | MPC | 15657 | Badger-Stafford-Malung 69 kV Rebuild |  | MN | MN |  | Other |  | Age and Condition | 2019-12-31 | 2019-12-31 | 69 | 0 | Y | 5300000 | Bottom-Up
A in MTEP20 | B>A | West | MPC | 17144 | Erie Area 69/41.6 kV Upgrades | This project provides new service to the Detroit Lakes area via the construction of a new 41.6 kV source (from the MPC Ulrich substation). The Ulrich-Westbury 69 kV circuit will be changed to a 69 and 41.6 kV double circuit. The 41.6 kV circuit will go to Audubon substation (which will need to be converted), and the 69 kV circuit will continue onto Richwood substation. Approximately 2.5 miles of 41.6 kV line will be built from Audubon to the Otter Tail Power 41.6 kV system. At that point, a new three-way switch will be constructed, and the Erie substation will be transferred onto Ulrich (saving $140,000 per year in wheeling costs, and improving load management signal strength at Erie). The Ulrich substation will also need a new 41.6 kV bay and breaker. Backup service from a new Audubon-Badoura 230 kV Tap (Erie Jct.) and associated 7 mile 41.6 kV line will allow for redundant alternate service. Depending on agreement language Erie may be able to be normally served from Ulrich or Erie Jct. | MN | MN | There is about 10 MW of load in the Detroit Lakes, MN area served by one substation (Erie) on the OTP 41.6 kV system. Extended outage times have been required for planned maintenance and emergency repairs because no alternate source is available. This is a concern for the Detroit Lakes, MN area. |  |  |  | 2022-12-31 | 2022-12-31 | 41.6 | 0 | Y | 5310000 | Bottom-Up
A in MTEP20 | B>A | South | SMPA | 18231 | West Owatonna - 69 kV breakers and relaying | replacement of (3) aging breakers along with new relaying | MN | MN | Replacement needed due to age of the breakers |  |  |  | 2020-12-31 | 2020-12-31 | 69 | 0 | Y | 850000 | Bottom-Up
A in MTEP20 | B>A | South | SMPA | 18234 | Preston - 69kV line rebuild | Rebuild existing 69kV transmission line. | MN | MN | Needed due to age of the line. |  |  |  | 2020-03-31 | 2020-03-31 | 69 | 0 | Y | 780000 | Bottom-Up
A in MTEP20 | B>A | South | SMPA | 18235 | Blooming Prairie - 69kV line rebuild | Rebuild existing 69kV line | MN | MN | rebuild needed due to age. |  |  |  | 2020-12-31 | 2020-12-31 | 69 | 0 | Y | 1750000 | Bottom-Up
A in MTEP20 | B>A | West | XEL | 15877 | East Metro Area Upgrades | To remediate overloads and voltage concerns in the East metro, line connections will be reconfigured at Red Rock, 115kV line from Afton - Red Rock will be upgraded. | MN | MN | In summer peak conditions, loss of the King transformer and either the Baytown-Long Lake 115 kV line or the Red Rock-Afton 115 kV line there are thermal overloads in the eastern Twin Cities area as well as several thermal and voltage concerns in the western Wisconsin area. | BRP |  |  |  |  | 115 | 0 | Y |  | Bottom-Up
A in MTEP20 | B>A | West | XEL | 17985 | Rosemount 2nd XFMR | Add second 115/34.5 kV transformer to Rosemount Substation | MN | MN | Needed to remediate distribution load at risk for single contingency |  |  |  | 2020-12-15 | 2020-12-15 | 115 | 34.5 | Y | 1200000 | Bottom-Up
A in MTEP20 | B>A | West | XEL | 17989 | EREPC Wellington Interconnection | Install new 3 way switch and 4 mile 69Kv line to new EREPC Wellington substation | MN | MN | Interconnection for new EREPC Wellington substation. |  |  |  | 2020-09-01 | 2020-09-01 | 69 | 0 | Y | 1320000 | Bottom-Up
A in MTEP20 | B>A | West | XEL | 18029 | West St Cloud - Millwood 69kV Rebuild | Rebuild 24 miles of 69kV line from West St. Cloud - Millwood to remediate aging condition issues | MN | MN | Rebuild 24 miles of 69kV line from West St. Cloud - Millwood to remediate reliability issues from aging condition of line. |  |  |  | 2021-06-01 | 2021-06-01 | 69 | 0 | Y | 10400000 | Bottom-Up
A in MTEP20 | B>A | West | XEL | 18033 | Hydro Lane Expansion | Expand Hydro Lane substation to support increased customer load | MN | MN | New customer load addition exceeds current capacity of Hydro Lane substation. |  |  |  | 2020-05-15 | 2020-05-15 | 69 | 12.5 | Y | 350000 | Bottom-Up
A in MTEP20 | B>A | West | XEL | 18132 | Cottage Grove Airgas Load Interconnection | New 115kV in and out substation tapped on Chemolite to Cottage Grove 115kV line to serve new Airgas load interconnection | MN | MN | New 115kV substation needed in Cottage Grove to serve new Airgas load interconnection. |  |  |  | 2020-10-01 | 2020-10-01 | 115 | 13.8 | Y | 5000000 | Bottom-Up
A in MTEP20 | B>A | West | XEL | 18344 | J587 Blazing Star 2 | New 200MW wind generation interconnection with new 345kV - 115kV substation and generation facilities. | MN | MN | System upgrades needed to accommodate new 200MW wind generation | GIP |  |  | 2020-09-15 | 2020-09-15 | 345 | 115 | Y | 3104000 | Externally Driven
A in MTEP20 | B>A | West | XEL | 18345 | Scott County - Helena Line Upgrade | Upgrade Helena - Scott County 345kV line to accommodate additional flow from J587 Blazing Star 2 generation interconnection | MN | MN | Additional capacity needed for Affected Systems Upgrade for J587 Blazing Star 2 generation interconnection. |  |  |  | 2022-09-15 | 2022-09-15 | 345 | 0 | Y | 34000000 | Bottom-Up
A in MTEP19 | B>A | West | GRE | 14364 | Swenoda 115 kV Substation | Install a 3-way, 115 kV switch on GRE’s AG-BK line and construct about 3 mile of 115 kV line with 477 ACSR conductor from the new 3-way switch to Agralite Electric Cooperative (AEC) Swenoda distribution substation. Previously known as Cashel West. | MN | MN | AEC needs Swenoda substation to serve a new spot load of 2 MW and pick up additional load that is now served from the Cashel 41.6 kV substation. | Other |  | Load Growth | 2019-02-19 | 2019-02-19 | 115 | 0 | Y | 1620000 | Bottom-Up
A in MTEP19 | B>A | West | GRE | 14365 | Dublin 115 kV Substation | Install a 3-way 115 kV switch on GRE’s AG-BK line, and construct about one span of 115 kV line with 477 ACSR conductor from the new 3-way switch to Agralite Electric Cooperative (AEC) Dublin distribution substation. Previously known as Cashel East. | MN | MN | AEC needs to construct the Dublin substation to serve all the Cashel 41.6 kV substation load that will not be served from Swenoda substation, provide contingency back to the Swenoda substation, and facilitate the retirement of the Cashel 41.6 kV substation. Cashel 41.6 kV substation will be retired due to age and condition. | Other |  | Load Growth | 2020-02-28 | 2020-02-28 | 115 | 0 | Y | 570000 | Bottom-Up
A in MTEP19 | B>A | West | GRE | 15744 | PD Line Rebuild | Rebuild 5.18 miles of the GRE PD 69 kV line from Harry Maser to the GRE EC-PAX line. | MN | MN | The 69 kV GRE PD line was built in 1952 and is in need of rebuild due to age and condition. Rebuilding the 5.18 mile stretch of the PD line to a larger conductor also has some operational benefits. | Other |  | Age and Condition | 2020-06-01 | 2020-06-01 | 69 | 0 | Y | 2519681 | Bottom-Up
A in MTEP19 | B>A | West | GRE | 15745 | Lake Eunice 115 kV Conversion | Convert the Lake Region Electric Cooperate (LREC) owned Lake Eunice substation from 41.6 kV service to 115 kV service. | MN | MN | Reduce the radial line exposure of the Lake Eunice 41.6 kV substation by converting it to 115 kV service. | Other |  | Reliability | 2020-10-30 | 2020-10-30 | 115 | 0 | Y | 1656000 | Bottom-Up
A in MTEP19 | B>A | West | GRE | 15764 | Lismore 115 kV Interconnection | Move the Nobles Cooperative Electric's Lismore substation load from the 24 kV line between Fulda and Magnolia to the Fenton-Nobles 115 kV line and provide support to remaining 24 kV system with 115 kV interconnection. | MN | MN | The Nobles Cooperative Electric requires 115 kV service for their Lismore substation. | Other |  | Load Growth | 2020-10-30 | 2020-10-30 | 115 | 0 | Y | 1628936 | Bottom-Up
A in MTEP19 | B>A | West | GRE | 15773 | Blaine II Substation | Add a second distribution transformer to serve the Blaine II distribution substation. | MN | MN | Connexus Energy requires additional capacity in the Blaine area. | Other |  | Load Growth | 2019-11-29 | 2019-11-29 | 69 | 0 | Y | 871000 | Bottom-Up
A in MTEP19 | B>A | West | GRE | 15775 | Arrowhead Reliability Upgrades | Add motor operators to existing disconnect switches at Schroeder SS2558, Lutsen SS2877 and Taconite Harbor 42NS2. Add reactive support to the Arrowhead 69 kV system (switchable reactors or STATCOM). | MN | MN | Reduce transmission outage times. Provide additional reactive support. | Other |  | Reliability | 2019-11-29 | 2019-11-29 | 69 | 0 | Y | 1400000 | Bottom-Up
A in MTEP19 | B>A | West | GRE | 15778 | Dickinson breaker 62JB3 & JB4 | Replace breakers 62JB3 & JB4 at Dickinson 345 kV | MN | MN | Age and condition | Other |  | Age and Condition | 2020-07-01 | 2020-07-01 | 345 | 0 | Y | 1250000 | Bottom-Up
A in MTEP19 | B>A | West | GRE | 15781 | Small Capital Projects and Asset Renewal - 2019 | Small Capital Projects and Asset Renewal - 2019 Breaker replacements: $730,048 Meter replacements: $1,050,000 RTU replacements: $499,000 Relay replacements: $1,558,451 Switch replacements: $496,893 | MN | MN | Age and condition | Other |  | Age and Condition | 2019-12-31 | 2019-12-31 | 230 | 0 | Y | 4334392 | Bottom-Up
A in MTEP19 | B>A | West | GRE | 15782 | Frog Creek 69 kV Bypass Switch | Install a one-way manually operated 69 kV switch at the intersection of Dahlberg Light and Power's 69 kV line and Great River Energy's BW line. | MN | MN | Provide a maintenance and emergency source to the GRE load served from Frog Creek. | Other |  | Other Local Needs | 2019-06-05 | 2019-06-05 | 69 | 0 | Y | 400000 | Bottom-Up
A in MTEP19 | B>A | West | GRE, MRES, OTP | 15344 | Erie Jct to Frazee Project | A new Erie Jct. 230/115 kV Substation will tap the Audubon to Hubbard 230 kV line about 16 miles east of Audubon. The Erie Jct. Substation will be in a ring bus configuration. There will be a new 115 kV line about 9 miles long from the Erie Jct. Substation to the existing Frazee Substation. The Frazee Substation will be rebuilt into a ring bus configuration and a 30 MVAR capacitor bank will also be added. | MN | MN | The project is needed as a result of native load growth and Hoot Lake Generation(140 MWs) retiring in 2021. The Western Minnesota Study analyzed the impacts of the Hoot Lake Generation retiring in the area. The study showed that several P1, P2 and P5 contingencies at the Audubon bus resulted in low voltages and overloads in the area. The study identified the Erie Jct. to Frazee project as the most efficient project to mitigate the concerns in the area caused by the retirement of Hoot Lake Generation. | BRP |  |  | 2023-11-30 | 2023-11-30 | 230 | 41.6 | Y | 16950000 | Bottom-Up
A in MTEP19 | B>A | West | GRE, MRES, OTP | 17006 | OTP-MRES-GRE Ortonville-Johnson Jct-Morris 115 kV Network Upgrades-J493/J526 | This project consists of upgrades to Otter Tail Power Company’s Ortonville to Morris 115 kV transmission line to accommodate the interconnection of wind generators, J493/J526. These facilities consist of: 1. OTP Ortonville to Johnson Jct. 115 kV line - ISD 10/30/2019 2. OTP Johnson Jct. to Morris 115 kV line - ISD 10/30/2019 3. OTP Ortonville Substation - ISD 8/21/2019 4. MRES Ortonville to Johnson Jct 115 kV line- ISD 12/1/2021 5. GRE Johnson Jct. to Morris 115 kV line- ISD 9/30/2021 | MN | MN | Network Upgrades to the Transmission Owner’s transmission line required for the interconnection of the Interconnection Customers’ Project J493/J526. | GIP |  |  | 2019-08-21 | 2021-12-01 | 115 | 0 | Y | 26728127 | Externally Driven
A in MTEP19 | B>A | West | MMPA | 17584 | MN River Breaker Install (position 5M421) | Install breaker on MN River Substation ring bus (position 5M421) | MN | MN | Fault on generator bus can result in partial loss of load | Other |  | Reliability | 2020-03-31 | 2020-03-31 | 115 | 0 | Y | 300000 | Bottom-Up
A in MTEP19 | B>A | West | MP | 7913 | 868 Line Upgrade | Increase capacity of Little Falls - West St. Cloud 115 kV Line | MN | MN | Post-contingent loading for multiple outage scenarios | BRP |  |  | 2019-12-31 | 2022-04-01 | 115 | 0 | Y | 6910000 | Bottom-Up
A in MTEP19 | B>A | West | MP | 10285 | Forbes Tie Breaker Addition | Reconfigure Forbes 115 kV bus to accommodate redundant bus tie breakers | MN | MN | Tie breaker failure disconnects entire Forbes 115 kV bus, causing low voltages in surrounding area. Also, fault on Forbes Bus 2 followed by failure of the bus tie breaker to operate causes overloads on adjacent 115 kV circuits. Redundant tie breakers will prevent tripping of entire Forbes 115 kV bus and transmission line remote ends, mitigating low voltage and overload issues. | BRP |  |  | 2020-12-31 | 2020-12-31 | 115 | 0 | Y | 2200000 | Bottom-Up
A in MTEP19 | B>A | West | MP | 13143 | 18 Line Upgrade | Reconductor ETCO - Forbes 115 kV Line and replace limiting substation equipment at Forbes and ETCO | MN | MN | Post-contingent overload following loss of a parallel line | BRP |  |  | 2018-12-31 | 2018-12-31 | 115 | 0 | Y | 1881000 | Bottom-Up
A in MTEP19 | B>A | West | MP | 15590 | 11 Line Upgrade | Thermal upgrade of Grand Rapids - Riverton 115 kV Line | MN | MN | Mitigate post-contingent overloading following loss of parallel 230 kV and 500 kV lines | BRP |  |  | 2021-05-01 | 2021-05-01 | 115 | 0 | Y | 3000000 | Bottom-Up
A in MTEP19 | B>A | West | MP | 15591 | Forbes 37 Line Upgrade | Increase rating of Forbes - 37 Line Tap 115 kV Line | MN | MN | Post-contingent overloads for loss of various parallel circuits | BRP |  |  | 2022-03-31 | 2022-03-31 | 115 | 0 | Y | 940000 | Bottom-Up
A in MTEP19 | B>A | West | MP | 15596 | Long Prairie Substation Modernization | Replace existing Long Prairie 115/34.5 kV 1TR and 2-3TR with higher-capacity LTC transformers; also replace existing 115 kV breakers and associated equipment. | MN | MN | Age & condition. Post-contingent overloading of existing Long Prairie transformers for loss of parallel transformer, including bus faults and line faults due to line-connected transformer configuration. Low post-contingent 34.5 kV bus voltage following 115 kV bus fault event mitigated by including LTCs on new transformers. | Other |  | Reliability | 2021-12-31 | 2021-12-31 | 115 | 34.5 | Y | 1700000 | Bottom-Up
A in MTEP19 | B>A | West | MP | 15597 | Savanna Transformer | Install new 115/13.8 kV transformer and breaker at existing Savanna Switching Station, retire 90 year Floodwood transformer. Replace existing Meadowlands transformer with new larger 115/13.8 kV transformer. | MN | MN | Age and condition of existing Floodwood and Meadowlands transformers. Enhance backup capability between Floodwood area and Meadowlands area to improve reliability and limit need to deploy mobile substation. | Other |  | Age and Condition | 2020-12-31 | 2020-12-31 | 115 | 13.8 | Y | 2500000 | Bottom-Up
A in MTEP19 | B>A | West | MP | 15601 | Midway Substation Retirement | Build out a new feeder from Canosia Road Substation to tie in to Midway feeders, then retire and remove Midway Substation. | MN | MN | Age & condition, maintenance issues with existing Midway Substation, and lack of full backup capability for Midway feeders | Other |  | Age and Condition | 2019-12-31 | 2019-12-31 | 115 | 13.8 | Y | 1200000 | Bottom-Up
A in MTEP19 | B>A | West | MP | 16804 | 38 Line Upgrade | Re-conductor transmission line to increase line rating. | MN | MN | Increased capacity to North Shore Loop | BRP |  |  | 2021-03-30 | 2021-03-30 | 115 | 0 | Y | 9860000 | Bottom-Up
A in MTEP19 | B>A | West | MPC, OTP | 4232 | NW Minnesota Projects | Winger Sub expansion to accommodate 2nd 230-115 kV transformer, 115 kV capacitors at Donaldson and Thief River Falls, automatic UVLS at Crookston, Donaldson, and Plummer by early 2020. Replace disconnects and Winger and switch at Plummer 115 kV to increase facility ratings. | MN | MN | Support Load Growth in North West Minnesota with a new 230 kV source - | BRP |  |  | 2019-12-31 | 2021-11-30 | 230 | 41.6 | Y | 12370000 | Bottom-Up
A in MTEP19 | B>A | West | MRES | 15818 | Willmar Sub Strain Bus Replacement | Willmar Municipal Utilities is replacing strain bus, jumpers, and switches at the Willmar Substation on the 69 kV bus. | MN | MN | The replacement is due to age and to increase capacity. | Other |  | Age and Condition | 2019-12-01 | 2019-12-01 | 69 | 0 | Y | 164000 | Bottom-Up
A in MTEP19 | B>A | West | MRES, OTP | 17225 | Norcross 115/41.6 kV Substation and 115 kV Line | The Norcross 115/41.6 kV Substation project will consist of building 7 miles of 115 kV lines from MRES's Grant County substation due west to where it intersects with OTP's 41.6 kV system. Near the intersection, a 115 / 41.6 kV substation will be constructed with a single high side breaker, a 41.6 kV tie breaker and 2-41.6 kV line breakers. | MN | MN | Load growth and new large loads are creating low voltage issues on the 41.6 kV system from Elbow Lake to Morris, specifically at ER's Wendell and OTPs Nashua. East River's Wendell substation will have a new dairy load in Fall of 2019 and OTP's Nashua will have a new elevator load that will likely come online in 2020. This area will see many hours at risk as defined in the Wendell Interconnection and Nashua Elevator Load Serving Study. | Other |  | Load Growth | 2020-12-15 | 2020-12-15 | 115 | 41.6 | Y | 11800000 | Bottom-Up
A in MTEP19 | B>A | West | OTP | 15725 | Hoot Lake 115 kV Cap Banks | Install two stages of 25 Mvar cap banks on the Hoot Lake 115 kV bus. | MN | MN | The 2x25 Mvar cap banks at Hoot Lake are needed for voltage support driven by the higher than average load growth in the area and the upcoming retirement of the Hoot Lake #2 and #3 generators. | Other |  | Age and Condition | 2021-05-01 | 2021-05-01 | 115 | 0 | Y | 2000000 | Bottom-Up
A in MTEP19 | B>A | West | RPU | 15951 | Marion Load Serving Substation | New 161/13.8 kV local load serving Substation built into existing RPU 161 kV transmission line. | MN | MN | Load growth in the RPU load serving area dictated the need for a new 161/13.8 kV local load serving substation | Other |  | Load Growth | 2021-06-01 | 2021-06-01 | 161 | 13.8 | Y | 8000000 | Bottom-Up
A in MTEP19 | B>A | West | SMPA | 16065 | West Owatonna Substation - 161kV Load Interconnection | Re-configuring the existing 161 kV yard to a ring and installing a new 161kV/12.5kV 50MVA transformer in SMMPA's West Owatonna Substation. | MN | MN | Owatonna Public Utilities (OPU) is acquiring 8-10MW of existing load from the Steele-Waseca Co-op. This load is currently being served from the 69kv bus at Owatonna, but will now be served from the 161kV bus as part of this project. | Other |  | Load Growth | 2019-12-02 | 2019-12-02 | 161 | 0 | Y | 1500000 | Bottom-Up
A in MTEP19 | B>A | West | SMPA | 17465 | Breaker Replacement - Byron | (3) 345kV breakers are being replaced at the Byron substation due to age. As a part of this replacement the CTs on the 345kV breakers will be upgraded to 2000A to match the ratings of the lines connected to the 345kV ring bus. | MN | MN | The primary driver for this project is the age of the breakers. | Other |  | Age and Condition | 2019-12-13 | 2019-12-13 | 345 | 0 | Y | 1500000 | Bottom-Up
A in MTEP19 | B>A | West | XEL | 15544 | Forbes Capacitor Reconfiguration | Project being performed as part of Forbes SVC retirement. Will replace 2X 300MVAR fixed capacitors at Forbes 500kV with 2X 160MVAR switched capacitors at Forbes 500kV | MN | MN | Provides necessary voltage control flexibility in area supporting Forbes SVC retirement. | Other |  | Other Local Needs | 2020-06-01 | 2020-06-01 | 500 | 0 | Y |  | Bottom-Up
A in MTEP19 | B>A | West | XEL | 15715 | Upgrade Waterville TR2 | Split 69kV bus by adding a new breaker. | MN | MN | Supports upgrade of Waterville TR2. Waterville TR2 is overloaded and in degraded condition upon loss of TR1. Additional customer load is expected in the near future and will overload existing transformer. | Other |  | Load Growth | 2019-06-15 | 2019-06-15 | 69 | 23.9 | Y | 940000 | Bottom-Up
A in MTEP19 | B>A | West | XEL | 15730 | South Afton Substation | Install feeders from 115kV line 0817 from Red Rock to Crystal Cave to new South Afton Substation. Install new 115kV breakers and bus work at new South Afton Substation. | MN | MN | Continued load growth is exceeding the capacity of Woodbury and Afton substations and additional capacity is needed. | Other |  | Load Growth | 2020-10-15 | 2020-10-15 | 115 | 34.5 | Y | 1100000 | Bottom-Up
A in MTEP19 | B>A | West | XEL | 16145 | Running Capacitor Retirement | One of the Six 30.5MVAR capacitor banks at running has failed and will be retired instead of repairing it. The remaining 5 are sufficient for providing voltage support in the area. | MN | MN | One of the Six 30.5MVAR capacitor banks at running has failed and will be retired instead of repairing it. The remaining 5 are sufficient for providing voltage support in the area. | Other |  | Other Local Needs | 2019-01-01 | 2019-01-01 | 230 | 0 | Y | 0 | Bottom-Up
A in MTEP19 | B>A | West | XEL | 16724 | Hazel Creek Transformer Upgrade | This project will upgrade 230kV/345kV Hazel Creek TR9 to accommodate J460 Blazing Star 1 generation interconnection. | MN | MN | The current transformer shows up as overloading under contingency once Blazing Star 1 is interconnected. This project will upgrade the transformer to accommodate the additional flows from the new generation. | GIP |  |  | 2020-09-01 | 2020-09-01 | 345 | 230 | Y | 4445000 | Externally Driven
B in MTEP20 | B | West | GRE, MRES | 17996 | Willmar 230/115 kV Transformer | Add a 230/115 kV LTC transformer at Willmar substation. | MN | MN | Low voltage during loss of Morris - Morris OTP 115 kV line. Better load sharing between Priam 115/69 kV transformer and Willmar 230/69 kV transformer. |  |  |  | 2021-06-01 | 2021-06-01 | 230 | 115 | Y | 10404000 | Bottom-Up
B in MTEP20 | B | West | MP | 18058 | Square Butte - Arrowhead HVDC Resiliency Upgrades | Structure replacements to improve HVDC line resiliency and restorability at critical locations, including transportation and infrastructure crossings. | ND | MN | Resiliency |  |  |  | 2025-12-31 | 2025-12-31 | 250 | 0 | Y | 10000000 | Bottom-Up
B in MTEP20 | B | West | MP | 18066 | Badoura Breaker Replacements | Replace existing 115 kV breakers at Badoura Substation | MN | MN | Age & condition |  |  |  | 2022-12-31 | 2022-12-31 | 115 | 0 | Y | 700000 | Bottom-Up
B in MTEP20 | B | West | OTP | 17987 | OTP Pelican Rapids 115kV Switch Replacement | Replace 400 Amp kV Switch at Pelican Rapids with 2,000 Amp kV Switch | MN | MN | Studies show an overload on the switch for various contingencies. |  |  |  | 2023-11-30 | 2023-11-30 | 115 | 0 | Y | 200000 | Bottom-Up
B in MTEP20 | B | West | XEL | 16524 | Medicine Lake Voltage Support | Put a new capacitor bank at Medicine Lake substation to provide voltage support in the area | MN | MN | Provides voltage support in the Medicine Lake, Bassett Creek area. |  |  |  | 2028-05-31 | 2028-05-31 | 115 | 0 | Y |  | Bottom-Up
B in MTEP19 | B | West | ITCM | 13888 | ITCM Walters 161/69kV Substation | Tap the Huntley - Freeborn 161kV line ~14 miles West of Freeborn and construct a ~7mi 161kV line and install a 100MVA 161-69kV transformer at the Walters Substation. | MN | MN | Voltage and Thermal overloads caused by separate P2.4 contingencies at Hayward and Huntley substations | Other |  | Reliability | 2021-12-31 | 2021-12-31 | 161 | 69 | Y | 11336139 | Bottom-Up
B in MTEP19 | B | West | MP | 15592 | Hibbing 14 Line Upgrade | Increase rating of Hibbing - 14 Line Tap 115 kV Line | MN | MN | Post-contingent overloads for loss of parallel circuits | BRP |  |  | 2021-05-01 | 2021-05-01 | 115 | 0 | Y | 1000000 | Bottom-Up
B in MTEP19 | B | West | MP | 15593 | 25 Line Upgrade | Increase rating of Hibbing - Virginia 115 kV Line | MN | MN | Post-contingent overloads under high transfer scenarios and multiple-circuit events | BRP |  |  | 2022-03-31 | 2022-03-31 | 115 | 0 | Y | 1200000 | Bottom-Up
B in MTEP19 | B | West | MP | 15594 | 29 Line Upgrade | Increase rating of Boswell - Grand Rapids 115 kV Line | MN | MN | Overloads following multiple circuit contingency events in surrounding area | BRP |  |  | 2021-05-01 | 2021-05-01 | 115 | 0 | Y | 750000 | Bottom-Up
B in MTEP19 | B | West | OTP | 16286 | Donaldson-Hallock 41.6 kV Line Upgrades | Repole and reinsulate 8.8 miles to a 69 kV level on the transmission line between Donaldson-Hallock 41.6 kV for reliability. | MN | MN | Age and condition of 8.8 miles between Donaldson to Hallock 41.6 kV transmission line will be repoled and reinsulated to a 69 kV level. | Other |  | Age and Condition | 2021-12-30 | 2021-12-30 | 41.6 | 0 | Y | 900000 | Bottom-Up
B in MTEP19 | B | West | OTP | 16287 | Nymore Tap 115 kV Line Upgrade | At the Nymore Tap 115 kV, approximately 3 miles of transmission line will be uprated from 69 kV line to 115 kV. | MN | MN | Due to load growth in the city of Bemidji, new 115 kV facilities are necessary to upgrade the level of service on the distribution system. | Other |  | Load Growth | 2023-12-30 | 2023-12-30 | 115 | 0 | Y | 1500000 | Bottom-Up
B in MTEP19 | B | West | OTP | 16288 | Bemidji 25th Street Tap 115 kV Upgrades | At the Bemidji 25th Street Tap 115 kV, approximately 3 miles of transmission line will be uprated from 69 kV line to 115 kV. | MN | MN | Due to load growth in the city of Bemidji, new 115 kV facilities are necessary to upgrade the level of service on the distribution system. | Other |  | Load Growth | 2023-12-30 | 2023-12-30 | 115 | 0 | Y | 1500000 | Bottom-Up
B in MTEP19 | B | West | OTP | 16289 | Bemidji 115/12.5 kV Substation | New Bemidji 115/12.5 kV Substation design with express feeders and source transfer, one transformer 37MVA/this is a multi-year project. | MN | MN | Due to load growth in the city of Bemidji, new 115 kV facilities are necessary to upgrade the level of service on the distribution system. | Other |  | Load Growth | 2020-12-30 | 2020-12-30 | 115 | 12.5 | Y | 8000000 | Bottom-Up
B in MTEP19 | B | West | OTP | 17444 | OTP Winger to Plummer 115 kV #2 | New 30 mile 115 kV transmission line from Winger to Plummer to support load growth in the NW Minnesota Region. | MN | MN | NW Minnesota pocket could have low voltage and thermal concerns for some contingencies. This line mitigates this concern. |  |  |  | 2028-11-30 | 2028-11-30 | 115 | 0 | Y | 16500000 | Bottom-Up
B in MTEP19 | B | West | XEL | 15742 | Goose Lake to MN Pipeline Upgrade | Upgrade 115kV line from Goose Lake to MN Pipeline. | MN | MN | Line is overloading under P7 contingency in the near term. | BRP |  |  | 2023-12-01 | 2023-12-01 | 115 | 0 | Y |  | Bottom-Up
A in MTEP20 | B>A | Central | AmerenMO | 4075 | Reconductor Sioux-Huster 138 kV line | Reconductor 5.9 miles of 954 kcmil ACSR with conductor capable of carrying 1600 A under summer emergency conditions. Replace 1200 A terminal equpment (dixconnect switches, CT's, bus conductor) at Huster with equipment capable of carrying 1600 A or better. | MO | MO | Line and Generator: Existing conductor would be loaded to about 104% of its rating for an outage to the Sioux-Belleau-6 345 kV Line with Callaway generation offline in 2021 summer, with 1-in-10 load levels, based on 2011 analysis. 109% loading in 2022 for EHV P6 and P2-3 criteria based on 2017 analysis. |  |  |  | 2023-06-01 | 2023-06-01 | 138 | 0 | Y | 5900000 | Bottom-Up
A in MTEP20 | B>A | Central | AmerenMO | 9721 | Bland-Tegeler 138 kV Reconductoring | Reconductor line to 1200 A summer emergency capability | MO | MO | Overload following 345 kV breaker failure. |  |  |  | 2020-06-01 | 2020-06-01 | 138 | 138 | Y |  | Bottom-Up
A in MTEP20 | B>A | Central | AmerenMO | 9733 | Page Breaker Replacment | Replace overstressed 138 kV breakers | MO | MO | Existing breakers are overstressed. |  |  |  | 2021-12-01 | 2021-12-01 | 138 | 138 | Y |  | Bottom-Up
A in MTEP20 | B>A | Central | AmerenMO | 9735 | Tyson Breaker Replacement | Replace overstressed 138 kV breakers | MO | MO | Existing breakers are overstressed. |  |  |  | 2021-12-01 | 2021-12-01 | 138 | 138 | Y |  | Bottom-Up
A in MTEP20 | B>A | Central | AmerenMO | 9830 | Reconductor Meramec-Joachim 138 kV line 2 | Reconductor to 1600 A summer emergency capability | MO | MO | Conductor loading projected to exceed rating following outage of two 345 kV lines. |  |  |  | 2022-06-01 | 2022-06-01 | 138 | 138 | Y |  | Bottom-Up
A in MTEP20 | B>A | Central | AmerenMO | 12428 | Replace Stoddard 161 kV breakers | Replace 1-161 kV breaker at Stoddard | MO | MO | Breaker fault duty |  |  |  | 2021-12-01 | 2021-12-01 | 161 | 0 | Y | 700000 | Bottom-Up
A in MTEP20 | B>A | Central | AmerenMO | 15268 | Upgrade Selma-Buck Knob 138 kV line (1302) | Upgrade the DPFE-SEL-1302 138 kV line from Selma Substation to the old Buck Knob substation location with conductor capable of 1600A under summer emergency conditions. Upgrade terminal equipment at Selma to 1600A minimum capability. | MO | MO | Age and condition of the structures and existing 4/0 copper condition necessitated the rebuild of the existing line. |  |  |  | 2021-06-01 | 2021-06-01 | 138 | 0 | Y |  | Bottom-Up
A in MTEP20 | B>A | Central | AmerenMO | 15487 | New Metal Container 138 kV Ring Bus | Install 4 position ring bus | MO | MO | Increased reliability per customer request. |  |  |  | 2022-06-01 | 2022-06-01 | 138 | 0 | Y |  | Bottom-Up
A in MTEP20 | B>A | Central | AmerenMO | 16487 | Marblehead North: Replace Terminal Equipment | Replace 1200A 138 kV switch, 1272 ACSR 138 kV bus conductor and 954 ACSR 161 kV bus conductor. | MO | MO | TMEP project to decrease congestion. |  |  |  | 2021-12-01 | 2021-12-01 | 161 | 138 | Y | 500000 | Bottom-Up
A in MTEP20 | B>A | Central | AmerenMO | 16504 | Reconfigure Viburnum 161/34 kV Substation | Install 2 161 kV line breakers and 1 161 kV circuit switcher on the transformer to split the CLK-CMCO-2 line and create 2 circuits into Viburnum Substation. | MO | MO | Eliminate concerns for droping the 34 kV mine area network due to a line outage of CLK-CMCO-2 |  |  |  | 2021-12-01 | 2021-12-01 | 161 | 34 | Y | 1313953 | Bottom-Up
A in MTEP20 | B>A | Central | AmerenMO | 16552 | Tyson Substation: Replace transformer 1 | Replace XFMR 1 with a hardened unit and replace the 138kV XFMR 1 breaker and Replace XFMR 3 breaker. | MO | MO | Security standard to install hardened unit and age and condition of existing XFMR breakers. |  |  |  | 2022-12-01 | 2022-12-01 | 345 | 138 | Y | 5071468 | Bottom-Up
A in MTEP20 | B>A | Central | AmerenMO | 16555 | Bugle Substation | Relocate the existing 138 kV Page substation to the new Bugle site. 138kV to be built as breaker and a half arrangement. | MO | MO | Increased reliability as well as future expansion of the 345 kV system |  |  |  | 2023-06-01 | 2023-06-01 | 138 | 0 | Y |  | Bottom-Up
A in MTEP20 | B>A | Central | AmerenMO | 16985 | Sioux-Meppen-4: Rebuild | Rebuild 3.7 mile Missouri side section (Str. 146-173) of the old Page-Keokuk line w/ T2 conductor. Page-Sioux-4: Rebuild Missouri River crossing (Str. 112-117) w/ 2000A rated conductor. | MO | MO | A field condition review of the lines revealed the need for structure and line conductor replacement due to age and condition. |  |  |  | 2023-12-01 | 2023-12-01 | 138 | 0 | Y | 2563177 | Bottom-Up
A in MTEP20 | B>A | Central | AmerenMO | 16986 | Page-Sioux-4: Rebuild Missouri River crossing | Rebuild existing Missouri River crossing (Str. 112-117) | MO | MO | A field condition review of the lines revealed the need for structure and line conductor replacement due to age and condition. |  |  |  | 2023-12-02 | 2023-12-02 | 138 | 0 | Y | 26657745 | Bottom-Up
A in MTEP20 | B>A | Central | AmerenMO | 17046 | Kelso Substation XFMR, breaker, and switch replacements | Install new 3000 A circuit breaker and motor-operated disconnect switch on 345 kV position V3. Replace the existing Kelso substation 336 MVA auto transformer #1 with a 560 MVA transformer. Replace the existing Kelso substation 161 kV bus tie 1-2 position H7 circuit breaker and bus disconnect switches. Replace the existing Kelso substation 161 kV position H6 circuit breaker and disconnect switch, upgrade the bus conductor of position H6 to achieve a minimum current carrying capability of 3000 A. Replace the existing Kelso substation H3 and H4 161 kV circuit breakers and disconnect switches in the CAPE-KEL-2 and KEL-MINR-2 terminals. Upgrade Kelso substation positions H3 and H4 bus conductors to achieve a minimum current carry capability of 2000 A. Replace the existing Kelso substation 161 kV disconnect switch on position H10. Replace the existing Kelso substation H11 and H12 161 kV disconnect switches (line and bus) in the CAPE-KEL-3) and KEL-MORLEY-3 terminals. | MO | MO | Age and condition of existing equipment with additions to increase reliability and operating flexibility. |  |  |  | 2022-12-01 | 2022-12-01 | 345 | 161 | Y | 5800000 | Bottom-Up
A in MTEP20 | B>A | Central | AmerenMO | 17065 | Tegeler 138 kV – Add and Replace Circuit Breakers | Install a new 2000 A circuit breaker and associated disconnect switches in the TGLR-BLAN-6756 138 kV line terminal. Replace the existing 1600 A circuit breaker and associated 1200 A disconnect switches and 1590 kcmil AAC bus conductor at position H5 with equipment capable of carrying 2000 A during summer emergency conditions. Increase relay load limit. Replace the existing 1200 A disconnect switches and 1590 kcmil AAC bus conductor in position H9 to match the capability of the 2000 A circuit breaker. Install 2 circuit switchers on the high-side of the new and existing 138/34.5 kV transformers, having a minimum continuous current rating of 600 A. | MO | MO | The bus-tie breaker replacement is needed due to age and condition. A line breaker is needed in the 138 kV TGLR-BLAN-6756 line to accommodate a second 138-34.5 kV transformer at Tegeler. Replace switches and bus conductor at position H9 to meet or exceed breaker ratings of 2000 A. |  |  |  | 2021-12-01 | 2021-12-01 | 138 | 0 | Y | 2100000 | Bottom-Up
A in MTEP20 | B>A | Central | AmerenMO | 17224 | Pershall 138-12.47 kV Substation | Install main-tie-main straight bus substation connecting to Berkeley-Sioux-1 and Berkeley-Sioux-2 lines. | MO | MO | Distribution load relief |  |  |  | 2021-06-01 | 2021-06-01 | 138 | 12 | Y |  | Bottom-Up
A in MTEP20 | B>A | Central | AmerenMO | 17344 | Berkeley Substation - Replace 138 kV bus tie 1-2 and 2-3 breakers | Replace 138 kV bus tie 1-2 and 2-3 breakers. Upgrade position to 2000A. | MO | MO | Age and condition of existing breakers. |  |  |  | 2021-12-01 | 2021-12-01 | 138 | 0 | Y |  | Bottom-Up
A in MTEP20 | B>A | Central | AmerenMO | 17346 | Rivermines: Replace Bus-tie breakers | Replace 138kV breakers on bus tie 1-2 and bus tie 2-3 | MO | MO | Age and condition of existing breakers. |  |  |  | 2022-12-01 | 2022-12-01 | 138 | 0 | Y |  | Bottom-Up
A in MTEP20 | B>A | Central | AmerenMO | 17605 | Page-Berkeley-1&2 Reconductor | Reconductor the Page-Berkeley-1&2 circuits with ACCR conductor | MO | MO | Increase clearances - age and condition. |  |  |  | 2022-12-01 | 2022-12-01 | 138 | 0 | Y |  | Bottom-Up
A in MTEP20 | B>A | Central | AmerenMO | 17624 | Pike 161 kV Substation - Ring bus addition | Rebuild the Pike 161 kV substation to a Ring bus configuration. | MO | MO | Increased reliability and operating flexibility in the area. |  |  |  | 2023-12-01 | 2023-12-01 | 161 | 0 | Y |  | Bottom-Up
A in MTEP20 | B>A | Central | AmerenMO | 17625 | McClay Substation: Add line breakers | Add breakers to each of the 138 kV lines and upgrade relays. | MO | MO | Increased reliability and operating flexibility. |  |  |  | 2022-12-01 | 2022-12-01 | 138 | 0 | Y |  | Bottom-Up
A in MTEP20 | B>A | Central | AmerenMO | 17629 | Ramona 138-12 kV substation | Install a new 138-12 kV substation tapping the Page-Berkeley 1 & 2 lines. | MO | MO | Distribution driven as part of the area 4-12 kV conversion. |  |  |  | 2023-12-01 | 2023-12-01 | 138 | 12 | Y |  | Bottom-Up
A in MTEP20 | B>A | Central | AmerenMO | 17665 | Barrett Station: Install 2nd 138-12 kV unit | Install 3 breakers in a main-tie-main configuration with an open bus tie to facilitate the installation of a 2nd transformer. Install circuit switchers on the existing and new transformers. | MO | MO | Distribution driven to serve load. |  |  |  | 2021-12-31 | 2021-12-31 | 138 | 12 | Y |  | Bottom-Up
A in MTEP20 | B>A | Central | AmerenMO | 17685 | Creve Coer 138-12 kV Substation | Tap the Mason-Meramec-1 & 2 lines to provide a main-tie-main configuration for new 138-12 kV substation. | MO | MO | Distribution driven for load growth |  |  |  | 2022-12-01 | 2022-12-01 | 138 | 12 | Y |  | Bottom-Up
A in MTEP20 | B>A | Central | AmerenMO | 17686 | Dougherty Ferry 138-12 kV Substation | Tap the Mason-Meramec-1 & 2 lines to provided a main-tie-main configuration for the installation of a new 138-12 kV substation. | MO | MO | Distribution driven to allow for the removal of the existing 34-12 kV station. |  |  |  | 2023-12-01 | 2023-12-01 | 138 | 12 | Y |  | Bottom-Up
A in MTEP20 | B>A | Central | AmerenMO | 17804 | Lutesville-St. Francois 345 kV Rebuild | Rebuild 63 miles of 345kV wood H-frame circuit. | MO | MO | Age and condition of existing facilities requires the rebuild of the line. |  |  |  | 2023-12-01 | 2023-12-01 | 345 | 0 | Y |  | Bottom-Up
A in MTEP20 | B>A | Central | AmerenMO | 17805 | CAMP-MLNE-1 & 2 Rebuild | Replace existing conductor with composite core conductor on branches 93 and 94. | MO | MO | Provided necessary increased capacity while maintaining acceptable clearances. |  |  |  | 2021-12-01 | 2021-12-01 | 138 | 0 | Y |  | Bottom-Up
A in MTEP20 | B>A | Central | AmerenMO | 17824 | Spencer Creek: Replace 345 kV switches | Replace switches on 345kv pos V3, V5, V6, V7 and reactor position. | MO | MO | Age and condition of existing switches. |  |  |  | 2021-12-01 | 2021-12-01 | 345 | 0 | Y |  | Bottom-Up
A in MTEP20 | B>A | Central | AmerenMO | 17829 | Loose Creek - Install shunt reactor | Install 345 kV shunt reactor at Loose Creek | MO | MO | High voltages during light load periods. |  |  |  | 2021-12-01 | 2021-12-01 | 345 | 0 | Y |  | Bottom-Up
A in MTEP20 | B>A | Central | AmerenMO | 17830 | Gasco-Osage-2: Replace shield wires | Replace both shield wires and replace structures as needed. | MO | MO | Age and condition of existing facilities. |  |  |  | 2021-12-01 | 2021-12-01 | 138 | 0 | Y |  | Bottom-Up
A in MTEP20 | B>A | Central | AmerenMO | 17865 | Lakeshire Breaker Replacement | Replace 40 kA breakers on positions H and U for cap banks 2A and 2B with 50 kA breakers. | MO | MO | General system expansion has increased the fault duty on these breakers, necessitating their replacement. |  |  |  | 2022-12-01 | 2022-12-01 | 138 | 0 | Y |  | Bottom-Up
A in MTEP20 | B>A | Central | AmerenMO | 17867 | Gray Summit Bus-Tie Breaker replacement | Replace the Bus-Tie 1-2 breaker at Gray Summit with a symmetrically rated 40 kA circuit breaker. | MO | MO | General system expansion has increased the fault duty on these breakers, necessitating their replacement. |  |  |  | 2022-12-01 | 2022-12-01 | 138 | 0 | Y |  | Bottom-Up
A in MTEP20 | B>A | Central | AmerenMO | 17908 | Bland-Franks-3 | Rebuild approximately 44 miles 345kV line to 3000A. | MO | MO | Age and condition of existing facilities. |  |  |  | 2024-12-01 | 2024-12-01 | 345 | 0 | Y |  | Bottom-Up
A in MTEP20 | B>A | Central | AmerenMO | 17909 | Campbell-Euclid-4- Replace shield wire | Replace shield wires on the Campbell-Euclid-4 circuit. Replace structures and crossarms as needed. | MO | MO | Age and condition of existing facilities. |  |  |  | 2021-06-01 | 2021-06-01 | 138 | 0 | Y |  | Bottom-Up
A in MTEP20 | B>A | Central | AmerenMO | 17945 | Hwy M Substation | Install 2 unit 138-12.47 kV substation on a site adjacent to the Dardenne Substation. | MO | MO | Distribution driven for local load serving needs. |  |  |  | 2024-12-01 | 2024-12-01 | 138 | 12.47 | Y |  | Bottom-Up
A in MTEP20 | B>A | Central | AmerenMO | 17947 | Fountain Lakes Substation 2nd unit | Add 2nd 138-12 kV unit at fountain Lakes Substation. | MO | MO | Distribution driven for local load serving needs. |  |  |  | 2023-12-01 | 2023-12-01 | 138 | 12.47 | Y |  | Bottom-Up
A in MTEP20 | B>A | Central | AmerenMO | 17969 | Replace Mason 345/138 kV Transformer | Replace 345/138 kV, 560 MVA Transformer #2 with a 700 MVA unit | MO | MO | N-1: outage of Sioux-Mason-7 345 kV |  |  |  | 2022-12-01 | 2022-12-01 | 345 | 138 | Y |  | Bottom-Up
A in MTEP20 | B>A | Central | AmerenMO | 18013 | Montgomery 345 kV - Install shunt reactor | Install 50 Mvar shunt reactor at Montgomery 345 kV substation. | MO | MO | High voltages experienced during light load periods. |  |  |  | 2025-12-01 | 2025-12-01 | 345 | 0 | Y |  | Bottom-Up
A in MTEP20 | B>A | Central | AmerenMO | 18016 | BERK-S-1 & 2 reconductor | Reconductor BERK-S-1 & 2 on branches 1004 and 1005 with composite core conductor. | MO | MO | Gain clearance from existing underbuild distribution. |  |  |  | 2023-12-01 | 2023-12-01 | 138 | 0 | Y |  | Bottom-Up
A in MTEP20 | B>A | Central | AmerenMO | 18056 | Mason shunt reactive device | Install a shunt Reactive device to control voltages at Mason 3 138 kV bus | MO | MO | Control local area voltages during various loading conditions. |  |  |  | 2023-12-01 | 2023-12-01 | 138 | 0 | Y |  | Bottom-Up
A in MTEP20 | B>A | Central | AmerenMO | 18139 | Labadie 345 kV bus-tie 2-3 Upgrade | Upgrade switches and CTs to 3000A. | MO | MO | 103.41% loading with N-1-1 outage for Labadie-Gray-2 and Mason-Labadie-4 in 2003LL case based on 2019 analysis. |  |  |  | 2022-12-01 | 2022-12-01 | 345 | 0 | Y |  | Bottom-Up
A in MTEP20 | B>A | Central | AmerenMO | 18158 | Loose Creek shunt reactive device | Install a shunt Reactive device to control voltages at Loose Creek 345 kV | MO | MO | Control local area voltages during various loading conditions. |  |  |  | 2022-12-01 | 2022-12-01 | 345 | 0 | Y |  | Bottom-Up
A in MTEP20 | B>A | Central | AmerenMO | 18267 | Wright City area 345 kV ring bus | Joint project between Ameren Missouri and AECI. Tap the Ameren Missouri Labadie-Montgomery 345kV line via a new 3-breaker, 345kV ring bus near the intersection of the line and the AECI (Central Electric Power Coop) 161kV line west of Charrette. Rebuild the existing 161kV line between the tap point and the AECI Wright City Substation as double-circuit 345/161kV. Install new 345/161kV step down transformer at Wright City. | MO | MO | Various P1, P2, P3, and P6 events typically involving the Enon and Belleau 345/161kV transformers and the Sioux-Belleau-6 345 kV line, result in loading issues, low voltages, and loss of load on the Ameren and AECI systems in Warren and St. Charles Counties based on 2019 analysis. |  |  |  | 2022-12-01 | 2022-12-01 | 345 | 161 | Y |  | Bottom-Up
A in MTEP20 | B>A | Central | AmerenMO | 18309 | Fredericktown Ring Bus | Install 138 kV ring bus at Fredericktown Substation | MO | MO | Increased reliability and operating flexibility. |  |  |  | 2022-12-01 | 2022-12-01 | 138 | 0 | Y |  | Bottom-Up
A in MTEP20 | B>A | Central | AmerenMO | 18312 | J817 Blue Bird Solar Generator Interconnection | Add terminal facilities at Warrenton 161 kV substation to interconnect J817, | MO | MO | Generator Interconnection. | GIP |  |  | 2020-09-01 | 2020-09-01 | 161 | 0 | Y |  | Externally Driven
A in MTEP20 | B>A | Central | AmerenMO | 18319 | FRDA-HRTG-7011 | Replace poles for OPGW installation. Structure replacements will increase the rating to 120 degrees C. | MO | MO | Facilitate the installation of OPGW - Age and condition of existing facilities. |  |  |  | 2021-12-01 | 2021-12-01 | 161 | 0 | Y |  | Bottom-Up
A in MTEP20 | B>A | Central | AmerenMO, WVPA | 17845 | Wittenberg-Trail of Tears 138 kV line | Wabash Valley- Install new Wittenberg ring bus switching station on the Grand Tower-Perryville line. Reconfigure Trail of Tears substation to BAAH. Install new 161 kV line from Trail of Tears to Charmin Bulk Substation. Install 2 breakers at Charmin Bulk Substation. Ameren - Install 12 miles of new 138 kV line from Wittenberg Substation to Trail of Tears Substation. Install new 161-138 kV transformer at Trail of Tears Substation. | MO | MO | Increased reliability and local load serving needs. |  |  |  | 2023-12-01 | 2023-12-01 | 161 | 138 | Y |  | Bottom-Up
A in MTEP19 | B>A | Central | AmerenIL | 16564 | Rebuild Prest-Steelville 138 kV line (1476) | Rebuild Prest-Steelville-1476 line to 1600A minimum. | MO | MO | Age and condition of existing structures require the rebuild of the line. | Other |  | Age and Condition | 2020-12-01 | 2020-12-01 | 138 | 0 | Y | 11523119 | Bottom-Up
A in MTEP19 | B>A | Central | AmerenIL | 16785 | Rebuild North Decatur-Latham 138 kV line (1350) | Rebuild the North Decatur-Latham-1350 line from Latham to structure 586. | MO | MO | Age and condition of existing structures necessitated the rebuild of the line. | Other |  | Age and Condition | 2020-12-01 | 2020-12-01 | 138 | 0 | Y | 8624296 | Bottom-Up
A in MTEP19 | B>A | Central | AmerenMO | 7862 | Rebuild Buick Smelter 161 kV Substation (Galena Substation) | Install new 6 position ring bus near the exiting Buick Smelter site on the FLET-CMCO-1 and CLK-CMCO-2 lines. Install 2 breakers on the tap lines to Buick Smelter and rebuild the supply lines. | MO | MO | Condition of existing substation | Other |  | Age and Condition | 2020-12-01 | 2020-12-01 | 161 | 0 | Y | 10400000 | Bottom-Up
A in MTEP19 | B>A | Central | AmerenMO | 9728 | Upgrade Adair 161 kV Substation | Upgrade terminal equipment | MO | MO | Increase system reliability | Other |  | Reliability | 2018-09-01 | 2018-09-01 | 161 | 161 | Y | 3000000 | Bottom-Up
A in MTEP19 | B>A | Central | AmerenMO | 9731 | Replace Marshall 138 kV Breakers | SCOPE: Replace the 138 kV Bus-Tie 3-4 circuit breaker and two (2) 138 kV bus disconnect switches. Replace the 138 kV Bus-Tie 2-3 circuit breaker and two (2) 138 kV bus disconnect switches. Replace the 138 kV Bus-Tie 1-2 disconnect switches (2). Replace the 138 kV line breaker in Marshall Substation on the MASN-MERAMEC-2 138 kV line and two (2) 138 kV line disconnect switches. Replace the 138 kV line breaker in Marshall Substation on the MRSL-TYSN-2 138 kV line and two (2) 138 kV line disconnect switches. Add a 138 kV line breaker in Marshall Substation on the MRSL-TYSN-1 138 kV line and two (2) 138 kV line disconnect switches. Replace the CNTL-WAT-1 138 kV line breaker in Marshall Substation and two (2) 138 kV line disconnect switches. Add a 138 kV line breaker in Marshall Substation on the MASN-MERAMEC-1 138 kV line and two (2) 138 kV line disconnect switches. | MO | MO | The 138 kV Bus-Tie 3-4 circuit breaker is exposed to fault duty exceeding the circuit breaker short circuit rating by 8% and must be replaced. Both bus disconnect switches for the breaker shall be replaced permitting full 3000 amp capability of the bus tie position. The 138 kV Bus-Tie 2-3 circuit breaker, Bus-Tie 1-2 disconnect switches, MRSL-TYSN-2, MASN-MER-2, and the CNTL-WAT-1 breakers are being replaced due to age and condition of the breakers to permit full 2000 A capability (3000 A for Bus-Tie 2-3 breaker, Bus-Tie 1-2 disconnect switches). The MRSL-TYSN-1 and MASN-MER-1 line breakers are being added for increased reliability of the 138 kV system, increased operation flexibility, and to reduce misoperation potential. | Other |  | Reliability | 2020-12-01 | 2020-12-01 | 138 | 138 | Y | 4700000 | Bottom-Up
A in MTEP19 | B>A | Central | AmerenMO | 9732 | Mason Breaker Replacment | Replace overstressed Bus-Tie 1-2 138 kV breaker. | MO | MO | Existing breaker is overstressed. | Other |  | Reliability | 2021-12-01 | 2021-12-01 | 138 | 138 | Y | 900000 | Bottom-Up
A in MTEP19 | B>A | Central | AmerenMO | 11910 | Reconductor Page-Mason 138 kV lines (1-2 lines) | Reconductor 138 kV lines. | MO | MO | Age and condition | Other |  | Age and Condition | 2019-12-31 | 2019-12-31 | 138 | 0 | Y | 6000000 | Bottom-Up
A in MTEP19 | B>A | Central | AmerenMO | 12173 | Re-energize Miller-Zion 161 kV line | Install new breaker station at Zion. Install new 138/161 kV transformer, New breaker station to tie-in Bland-Osage-6030 and Gasco-Osage-2 138 kV lines at Miller. Restore the Miller-Zion 161 kV line to operation. | MO | MO | With Osage generation offline and the Maries-Osage 138 kV line out, area voltage support is needed, based on 2016 analysis work. | Other |  | Reliability | 2021-12-01 | 2021-12-01 | 161 | 138 | Y | 15600000 | Bottom-Up
A in MTEP19 | B>A | Central | AmerenMO | 12425 | Replace Cape 161 kV breakers | Replace 3-161 kV Breakers | MO | MO | Replace due to fault duty | Other |  | Reliability | 2019-12-01 | 2019-12-01 | 161 | 0 | Y | 1500000 | Bottom-Up
A in MTEP19 | B>A | Central | AmerenMO | 14884 | New Dillon 138 kV substation ring bus | Install initial 5 position ring bus near the west tap to Alfermann Substation. Split the Clark-Osage-2 line and route in and out of the ring bus. Split the Rivermines-Maries-1 138 kV line and terminate the western section (from Maries) into the ring bus and connect the eastern section to a 28 MVAR capacitor bank to be located at Dillon. Disconnect the line to Alfermann (to be acquired by ATXI) from CLK-O-2 and terminate into the ring bus. Provide one position on the ring bus for AECI supply to Macedonia. Install minimum 2000 A, 138 kV bus tie breaker (to be owned by ATXI) at Rolla Municipal Utilities' Alfermann Substation. | MO | MO | Requested by Rolla Municipal Utilities (RMU). Provides increased reliability and operational flexibility for Ameren Missouri by segmenting the CLK-0-2 and RIV-MRES-1 double-circuit 138 kV lines. | Other |  | Reliability | 2020-06-01 | 2020-06-01 | 138 | 0 | Y | 10400000 | Bottom-Up
A in MTEP19 | B>A | Central | AmerenMO | 15329 | Rebuild St. Francios-Rivermines 138 kV lines 2 & 3 | Replace structures in order to permit and operating temperature of 110 degrees C from structure 254 to 307. | MO | MO | A field condition review revealed the need for structure replacements. | Other |  | Age and Condition | 2021-12-01 | 2021-12-01 | 138 | 0 | Y | 4900000 | Bottom-Up
A in MTEP19 | B>A | Central | AmerenMO | 15424 | New Franklin 138 kV substation breakers | Install 138 kV, 2000 A, 40 kA interrupting capability breakers at the Franklin terminals of the Gray-Franklin-1 and -2 138 kV lines. | MO | MO | P6-1-1 line+line event: For the outage of the Gray-Franklin-1 and-2 138 kV lines, the load served from Franklin and Tegeler Substations would be subject to load collapse. | BRP |  | Reliability | 2019-06-01 | 2019-06-01 | 138 | 0 | Y | 2400000 | Bottom-Up
A in MTEP19 | B>A | Central | AmerenMO | 15500 | Upgrade Troy-Pike 161 kV line | Upgrade clearances on the 161 kV TROY-PIKE-1 line for the sections from Auburn tap to Cyrene tap and Cyrene tap to Pike substation, to allow for a maximum operating temperature during summer conditions of 100°C. | MO | MO | A field condition review of the line revealed the need for structure replacements due to insufficient ground and obstacle clearances. | Other |  | Age and Condition | 2019-06-01 | 2019-06-01 | 161 | 0 | Y | 4100000 | Bottom-Up
A in MTEP19 | B>A | Central | AmerenMO | 15501 | Upgrade Belleau-Troy 161 kV line | Upgrade clearances on the 161 kV BELU-TROY-1 line for the section from Dardenne substation to Troy substation, section 53, to allow for a maximum operating temperature during summer conditions of 100°C. | MO | MO | A field condition review revealed the need for structure replacements. | Other |  | Age and Condition | 2019-06-01 | 2019-06-01 | 161 | 0 | Y | 2400000 | Bottom-Up
A in MTEP19 | B>A | Central | AmerenMO | 15503 | Rebuild Mason-Wildwood 138 kV lines 1 & 2 | Rebuild Conway-Clarkson section to 2000A. 7 structure replacements required on the Mason-Conway section. | MO | MO | Structure replacements required due to age and condition as well as clearance issues. | Other |  | Age and Condition | 2022-06-01 | 2022-06-01 | 138 | 0 | Y | 8000000 | Bottom-Up
A in MTEP19 | B>A | Central | AmerenMO | 15524 | Replace Sioux 345/138 kV transformer | Replace the existing 345-138 kV transformer with a new unit | MO | MO | Age and condition of the existing unit. | Other |  | Age and Condition | 2021-12-01 | 2021-12-01 | 345 | 0 | Y | 5000000 | Bottom-Up
A in MTEP19 | B>A | Central | AmerenMO | 15526 | Rebuild Mason–Meramec 1 & 2 138 kV lines | Replace six (6) steel lattice structures to permit operation of the existing conductor to 120°C in the 13.97 mile section from Marshall to Meramec in the Mason – Meramec – 1 and Mason – Meramec – 2 138 kV double-circuit line. Modify underbuild in 39 spans. Install OPGW from Marshall to Rudder. | MO | MO | A field condition review of the line revealed the need for structure replacements. | Other |  | Age and Condition | 2023-12-01 | 2023-12-01 | 138 | 0 | Y | 18700000 | Bottom-Up
A in MTEP19 | B>A | Central | AmerenMO | 16548 | New Hughes 138 kV Substation (J541) for wind Interconnection | Install new 4 position 345 kV ring bus for new generator interconnection | MO | MO | Interconnection facilities for the J541 High Prairie wind project | GIP |  |  | 2020-05-01 | 2020-05-01 | 345 | 0 | Y | 1000000 | Externally Driven
A in MTEP19 | B>A | Central | AmerenMO | 16549 | Upgrade Lincoln 161 kV Substation | Install 2 161 kV breakers and 3 161 kV disconnect switches including 1 motor operated switch. | MO | MO | Project needed to facilitate an AECI planned project to extend the Troy-Lincoln line to serve their Meister sub. | Other |  | Age and Condition | 2020-06-01 | 2020-06-01 | 161 | 0 | Y | 2700000 | Bottom-Up
A in MTEP19 | B>A | Central | AmerenMO | 16554 | Upgrade Maline 138 kV Substation | Replace bus tie 3-4 OCB, and pos S OCB. | MO | MO | Breakers to be replaced due to age and condition. | Other |  | Age and Condition | 2020-12-01 | 2020-12-01 | 138 | 0 | Y | 514048 | Bottom-Up
A in MTEP19 | B>A | Central | AmerenMO | 16684 | Rebuild Huster-Belleau 138 kV line | Rebuild HUST-BELU-3 to 1600A. Upgrade 2 138 kV switches and bus conductor at Huster to achieve 1600A capability. | MO | MO | Age and condition of the existing conductor. | Other |  | Age and Condition | 2020-06-01 | 2020-06-01 | 138 | 0 | Y | 3234446 | Bottom-Up
A in MTEP19 | B>A | Central | AmerenMO | 16786 | Replace Warson 161 kV Substation equipment | Replace Bus tie 1-2 and 3-4 breakers | MO | MO | Age and condition of existing breakers. | Other |  | Age and Condition | 2020-06-01 | 2020-06-01 | 138 | 0 | Y | 2000000 | Bottom-Up
A in MTEP19 | B>A | Central | AmerenMO | 16793 | Replace equipment at Montgomery 161 kV Substation | Replace bus-tie breaker 16102 and upgrade relays at Montgomery Substation. | MO | MO | Age and condition of existing equipment. | Other |  | Age and Condition | 2020-12-01 | 2020-12-01 | 138 | 0 | Y | 733069 | Bottom-Up
A in MTEP19 | B>A | Central | AmerenMO | 16795 | Replace Marion Tap-Marion 161 kV Structures | Replace structures on the Marion Tap-Marion section of the Peno-Creek-Spalding-2 line. | MO | MO | Age and condition requires the need to replace the existing structures. | Other |  | Age and Condition | 2020-12-01 | 2020-12-01 | 161 | 0 | Y | 554745 | Bottom-Up
B in MTEP20 | B | Central | AmerenMO | 17946 | Blanchette Substation 2nd unit | Add 2nd 138-34.5 kV unit at Blanchette Substation. | MO | MO | Distribution driven for local load serving needs. |  |  |  | 2026-12-01 | 2026-12-01 | 138 | 34.5 | Y |  | Bottom-Up
B in MTEP20 | B | Central | AmerenMO | 18063 | Maywood-Sub T Ring Bus Addition and Customer-Funded 69 kV Municipal Loop | At the request of Mt. Pleasant Municipal Utilities (MPMU), Ameren Missouri to construct three breaker, 345 kV substation west of Mt. Pleasant, Iowa, along Ameren Missouri's Maywood-Sub T Transmission Line. Ameren Transmission Company of Illinois (ATXI) to install 345/69 kV step-down transformer and construct 69 kV networked loop to interconnect MPMU's distribution substations. MPMU to fund 69 kV facilities. | MO | MO | Customer-Driver Request |  |  |  | 2023-12-31 | 2023-12-31 | 345 | 69 | Y |  | Bottom-Up
B in MTEP19 | B | Central | AmerenMO | 15326 | Rebuild Fletcher-Pilot Knob 161 kV line | Rebuild the Fletcher-Pilot Knob-2 161 kV line to 2000A. Upgrade the terminal position at Pilot Knob to 2000A | MO | MO | A field inspection of the line revealed the need to replace the majority of the structures due to age and condition. |  |  |  | 2023-12-31 | 2023-12-31 | 161 | 0 | Y | 37400000 | Bottom-Up
B in MTEP19 | B | Central | AmerenMO | 15327 | Rebuild Fletcher-Cominco 161 kV line | Rebuild the Fletcher-Cominco-1 161 kV line to 2000A. Upgrade terminal equipment at Brushy Creek to 2000A. | MO | MO | An inspection of the line revealed the need to replace the majority of the structures due to age and condition. |  |  |  | 2023-12-31 | 2023-12-31 | 161 | 0 | Y | 20400000 | Bottom-Up
B in MTEP19 | B | Central | AmerenMO | 15328 | Rebuild Clark-Cominco 161 kV line | Rebuild the Clark-Cominco-2 161 kV line to 2000A. Upgrade the terminal equipment at Clark Substation to 2000A. | MO | MO | An inspection of the line revealed the need to replace the majority of the structures due to age and condition. |  |  |  | 2023-12-31 | 2023-12-31 | 161 | 0 | Y | 27000000 | Bottom-Up
A in MTEP20 | B>A | Central | AmerenMO | 16491 | Rebuild Sioux-Meppen-4, Page-Sioux-4, Sioux-Huster-1 138 kV lines | Sioux-Huster-1/Sioux-Meppen North-4: Rebuild ~9 miles of triple circuit 138 kV lattice tower line to double-circuit steel poles. | MO,IL | MO,IL | A field condition review of the lines revealed the need for structure and line conductor replacement due to age and condition. |  |  |  | 2019-12-01 | 2019-12-01 | 138 | 0 | Y | 14229659 | Bottom-Up
A in MTEP20 | B>A | South | Entergy-MS | 17086 | Brandon Area Loop Project | Tap L540A (East Whitfield to South Brandon) with a 115kV GOAB and build a new 115kV transmission line from the South Brandon tap to East Brandon delivery point GOAB. | MS | MS | Member has requested loop service. |  |  |  | 2022-12-01 | 2022-12-01 | 115 | 0 | Y | 3770000 | Bottom-Up
A in MTEP20 | B>A | South | Entergy-MS | 18153 | Moorhead 115 kV: Install Cap Bank | Install 21.6 MVAR cap bank at Moorhead. | MS | MS | NERC TPL-001-4 Reliability Standards and Entergy's Planning Guidelines. P2.2 Loss of the Indianola 115 kV bus results in low voltage at Moorhead and Itta Bena substations. |  |  |  | 2021-12-01 | 2021-12-01 | 115 | 0 | Y | 2673377 | Bottom-Up
A in MTEP20 | B>A | South | Entergy-MS | 18258 | Batesville 115 kV: Upgrade Bus | Upgrade all 115 kV terminal equipment for the 230-115 kV autotransformer at Entergy's Batesville substation to a minimum rating of 3000 amps. Establish a 2 hour emergency rating of 130% on Entergy Mississippi’s Batesville 230-115 kV autotransformer. | MS | MS | NERC TPL-001-4 Reliability Standards and Entergy's Planning Guidelines. P2.3 CE Batesville breaker 161B11 failure results in thermal overloads on EMI Batesville’s 230/115kV auto. |  |  |  | 2022-06-01 | 2022-06-01 | 115 | 0 | Y | 3528322 | Bottom-Up
A in MTEP19 | B>A | South | Entergy-MS | 9823 | Franklin 500 kV reconfig | Reconfigure the Franklin 500 kV EHV substation so that the Franklin - Bogalusa and Franklin - McKnight 500 kV lines do not share a common breaker. | MS | MS | The loss of a common shared breaker (P2.3) between the Franklin - Bogalusa and Franklin - McKnight 500 kV lines results in multiple thermal overloads on the south Mississippi 115 kV system. | BRP |  |  | 2022-12-01 | 2022-12-01 | 500 | 0 | Y | 26339853 | Bottom-Up
A in MTEP19 | B>A | South | Entergy-MS | 13932 | Catlett Road - South Canton 230 kV: New line | Tap Bozeman – Tinnin Road 230 kV near the intersection of Highway 22 and Catlett Road, and build a new breaker station (Catlett Road). Build 5 mile 230kV line from Catlett Road to South Canton. | MS | MS | Enhanced Transmission Reliability. For the loss of McAdams - Pickens 230 kV and South Canton - Yandell Road 230 kV, approximately 50 MW of load is at risk. | Other |  | Reliability | 2022-12-01 | 2022-12-01 | 230 | 0 | Y | 58900000 | Bottom-Up
A in MTEP19 | B>A | South | Entergy-MS | 13955 | Northpark: Install 230/115 kV autotransformer | Install 3-phase, 400 MVA, 230-115 kV Auto at Northpark Substation | MS | MS | NERC TPL-001-4 Reliability Standards and Entergy's Local Planning Criteria. A P2.3 internal breaker fault at Lakeover 500kV substation causes thermal overloads on the Rex Brown 230/115kV auto. A P2.4 internal breaker fault J9753 at Rex Brown 115kV substation causes thermal overloads on the Northpark - Country Club 115 kV line section. | BRP |  |  | 2023-06-01 | 2023-06-01 | 230 | 115 | Y | 15600000 | Bottom-Up
A in MTEP19 | B>A | South | Entergy-MS | 13958 | Horn Lake 230/161 kV: Energize autotransformer | Energize the existing 230/161 kV auto at Horn Lake that is currently operated as Normally Open | MS | MS | Enhanced Reliability. The loss of the Getwell to Twinkletown and Freeport to Horn Lake 230 kV lines results in low voltages along the Getwell - Horn Lake 115 kV section. Mitigation requires up to 45 MW of load shed to alleviate the low voltage violations. | Other |  | Reliability | 2022-12-31 | 2022-12-31 | 230 | 161 | Y | 200000 | Bottom-Up
A in MTEP19 | B>A | South | Entergy-MS | 13959 | Fernwood 115 kV: Install transmission breakers | Install transmission breakers at Fernwood 115 kV substation | MS | MS | Enhanced Transmission Reliability. Installation of transmission breakers on the Kentwood (ELL) - McComb 115 kV circuit will improve customer performance along this transmission circuit which serves more than 10,000 customers. | Other |  | Reliability | 2019-12-15 | 2019-12-15 | 115 | 0 | Y | 5200000 | Bottom-Up
A in MTEP19 | B>A | South | Entergy-MS | 15624 | Half Mile 115kV Delivery Point | Serve the new load delivery point by rebuilding the Itta Bena 115kV switching station and adding breakers. Build a 115kV radial transmission line from the Itta Bena switching station to the Half Mile delivery point. | MS | MS | Member Coop has requested a new load delivery point in Leflore County, MS. | Other |  | Load Growth | 2021-08-01 | 2021-08-01 | 115 | 0 | Y | 8010000 | Bottom-Up
A in MTEP19 | B>A | South | Entergy-MS | 15625 | East Brandon 115kV Delivery Point | Add new 115 kV bay w/breaker to Rankin substation and build a new 115 kV transmission line from the Rankin substation to East Brandon delivery point GOAB. | MS | MS | Member Coop has requested a new load delivery point in Rankin County, MS. | Other |  | Load Growth | 2022-06-01 | 2022-06-01 | 115 | 0 | Y | 4260000 | Bottom-Up
A in MTEP19 | B>A | South | Entergy-MS | 15709 | Clinton 115 kV: Install Circuit Breakers | Install Transmission Breakers at Clinton 115 kV substation. | MS | MS | Enhanced Transmission Reliability Installation of transmission breakers on the The Ray Braswell EHV - Rex Brown SES Switchyard 115 kV circuit will improve customer performance along this transmission circuit which serves a large amount of customers. | Other |  | Reliability | 2025-12-31 | 2025-12-31 | 115 | 0 | Y | 6153278 | Bottom-Up
A in MTEP19 | B>A | South | Entergy-MS | 15710 | Cleveland 115 kV: Install Circuit Breakers | Install Transmission Breakers at Cleveland 115 kV substation. | MS | MS | Enhanced Transmission Reliability Installation of transmission breakers on the Delta SES Switchyard - Indianola 115 kV kV circuit will improve customer performance along this transmission circuit which serves a large amount of customers. | Other |  | Reliability | 2019-12-15 | 2019-12-15 | 115 | 0 | Y | 5700000 | Bottom-Up
A in MTEP19 | B>A | South | Entergy-MS | 15712 | South Jackson - Florence 115 kV: Terminal Equipment | Upgrade a 115 kV switch at the Florence substation in order to increase the through-path rating of the South Jackson - Florence 115 kV line to 260 MVA. | MS | MS | Reliability Standards and Entergy's Local Planning Criteria. A P1.2 loss of the TVA Choctaw - TVA Clay 500 kV transmisison line results in thermal overloads on the South Jackson - Florence 115 kV line section. | BRP |  |  | 2020-06-01 | 2020-06-01 | 115 | 0 | Y | 0 | Bottom-Up
A in MTEP19 | B>A | South | Entergy-MS | 15729 | Centreville 115 kV: Install Cap Bank | Install 10.8 MVAR capacitor bank at Centreville 115 kV substation. | MS | MS | NERC TPL-001-4 Reliability Standards and Entergy's Local Planning Criteria. Base case P0 low voltage at Woodville 115 kV. A P2.1 loss of the Liberty - Gloster 115 kV line section results in low voltage at Centreville and Woodville 115 kV. | BRP |  |  | 2020-12-01 | 2020-12-01 | 115 | 0 | Y | 1864841 | Bottom-Up
A in MTEP19 | B>A | South | Entergy-MS | 15845 | Woodville Loop Project | Tap the EMI owned Centreville to Woodville 115kV line with a switching station and build a new 115kV transmission line to EMI Harper switching station. | MS | MS | Current radial transmission service violates MW-Mile planning criteria. | Other |  | Reliability | 2023-03-01 | 2023-03-01 | 115 | 0 | Y | 11140000 | Bottom-Up
A in MTEP19 | B>A | South | Entergy-MS | 15847 | Utica JC Loop Project | Rebuild L516 (Utica to Utica JC) with sufficient ACSR conductor. Tap L516 with a 115kV GOAB and build a 115kV transmission line to Port Gibson substation. | MS | MS | Current radial transmission service violates MW-Mile planning criteria. | Other |  | Reliability | 2024-07-01 | 2024-07-01 | 115 | 0 | Y | 16685000 | Bottom-Up
A in MTEP19 | B>A | South | Entergy-MS | 15849 | Evans Loop Project | Tap L550 (Schlater to Evans) with a 115kV GOAB and build a new 115kV transmission line to Half Mile switching station. Add a new 115kV line bay to Entergy Mississippi's existing Schlater substation and install transmission line breakers. | MS | MS | Current radial transmission service violates MW-Mile planning criteria. | Other |  | Reliability | 2021-08-01 | 2021-08-01 | 115 | 0 | Y | 3335000 | Bottom-Up
A in MTEP19 | B>A | South | Entergy-MS | 16565 | J679 Interconnection: Construct 115 kV Switching Substation | Construct a 115kV 3 breaker ring bus on the Greenwood - Winona 115kV line. | MS | MS | The 3 breaker ring bus 115kV switching station is needed to interconnect the J679 solar facility. | GIP |  |  | 2021-04-15 | 2021-04-15 | 115 | 0 | Y | 2665000 | Externally Driven
A in MTEP19 | B>A | South | Entergy-MS | 16568 | Ruleville 115 kV: Install Transmission Line Bay and Breakers (J604 Interconnection) | Install breakers at the Ruleville 115kV substation. | MS | MS | The breaker station is needed to interconnect the J604 solar facility. | GIP |  |  | 2021-03-15 | 2021-03-15 | 115 | 0 | Y | 7381000 | Externally Driven
A in MTEP19 | B>A | South | SMEPA | 12212 | Oak Grove Delivery Point | In order to serve the Oak Grove delivery point economically and reliably, Line 91 (Okahola GOAB – Oak Grove) will be extended to the proposed Oak Grove 161/69kV substation for service and the temporary 69kV GOAB will be removed. | MS | MS | A member has requested transmission service from Cooperative Energy. | Other |  | Load Growth | 2021-12-01 | 2021-12-01 | 69 | 0 | Y | 0 | Bottom-Up
A in MTEP19 | B>A | South | SMEPA | 16604 | Oak Grove DP Temp | In order to serve the Oak Grove delivery point, Cooperative Energy’s Line 91 (Okahola GOAB – Oak Grove) will be rebuilt with 795 ACSR conductor. A temporary 69kV GOAB will be installed near the original location in Line 39/39B. A new 69/26.4kV, 15/20/25 MVA transformer will be installed at the Oak Grove substation to accommodate the 69kV service. | MS | MS | A member has requested transmission service from Cooperative Energy. | Other |  | Load Growth | 2019-12-01 | 2019-12-01 | 69 | 0 | Y | 2326650 | Bottom-Up
B in MTEP20 | B | South | Entergy-MS | 18144 | SE Natchez to Crosby 115 kV Line Rebuild | Rebuild SE Natchez to Crosby 115 kV line to a minimum through path rating of 1300A. Rebuild line sections to double circuit 230 kV specifications but only insulate and string one side. | MS | MS | Enhanced Reliability P1.2 Loss of Franklin to Arlington 115 kV line causes high thermal loading on the SE Natchez to Crosby 115 kV line section. |  |  |  | 2029-06-01 | 2029-06-01 | 115 | 0 | Y | 39526142 | Bottom-Up
B in MTEP20 | B | South | Entergy-MS | 18150 | Crosby to Harper 115 kV Line Rebuild | Rebuild Crosby to Harper 115 kV line to a minimum through path rating of 1300A. Rebuild line sections to double circuit 230 kV specifications but only insulate and string one side. | MS | MS | Enhanced Reliability. P1.2 Loss of Franklin to Arlington 115kV line causes high thermal loading on the Crosby to Harper 115kV line section. |  |  |  | 2031-06-01 | 2031-06-01 | 115 | 0 | Y | 11845519 | Bottom-Up
B in MTEP20 | B | South | Entergy-MS | 18156 | Hoy Road 230 kV: Install transmission breakers | Install transmission line breakers at the existing Hoy Road 230 kV substation. | MS | MS | Enhanced Reliability. The Yandell Rd - Lakeover 230 kV line is currently non-compliant with internal Entergy Standards. |  |  |  | 2028-06-01 | 2028-06-01 | 230 | 0 | Y | 13976994 | Bottom-Up
B in MTEP19 | B | South | Entergy-MS | 13961 | Plum Point 115 kV: Add Circuit Breakers | Add Transmission Breakers to the Plum Point 115kV Substation | MS | MS | Enhanced Transmission Reliability. The Getwell to Horn Lake 115kV line currently has greater than 10,000 customers between breaker stations and approximately 145MW of load. | Other |  | Reliability | 2025-12-31 | 2025-12-31 | 115 | 0 | Y | 5500000 | Bottom-Up
B in MTEP19 | B | South | Entergy-MS | 15708 | North Jackson 115 kV: Install Circuit Breakers | Install Transmission Breakers at North Jackson 115 kV substation. | MS | MS | Installation of transmission breakers on the Jackson Northeast - Rex Brown 115 kV circuit will improve customer performance along this transmission circuit which serves a large amount of customers. | Other |  | Reliability | 2024-12-01 | 2024-12-01 | 115 | 0 | Y | 1576531 | Bottom-Up
B in MTEP19 | B | South | Entergy-MS | 15711 | Florence 115 kV: Install Circuit Breakers | Install Transmission Breakers at Florence 115 kV substation. | MS | MS | Enhanced Transmission Reliability Installation of transmission breakers on the South Jackson - Magee 115 kV circuit will improve customer performance along this transmission circuit which serves a large amount of customers. | Other |  | Reliability | 2025-12-31 | 2025-12-31 | 115 | 0 | Y | 4739471 | Bottom-Up
B in MTEP19 | B | South | Entergy-MS | 15714 | Greenville - SE Greenville 115 kV: Line Rebuild | Rebuild existing Greenville - SE Greenville 115 kV line | MS | MS | Reliability Standards and Entergy's Local Planning Criteria. A P2.3 failure of a breaker at Gerald Andrus, and the P3 loss of the Baxter Wilson - Perryville 500 kV line coupled with the loss of Grand Gulf generation results in thermal overload on the Greenville - SE Greenville 115 kV transmission line. | BRP |  |  | 2023-06-01 | 2023-06-01 | 115 | 0 | Y | 3400000 | Bottom-Up
B in MTEP19 | B | South | Entergy-MS | 15848 | Jayess Loop Project | Rebuild L523 (Norfield SS to Little Creek) with sufficient ACSR conductor. Tap L549 (Jayess SS to Jayess) with a 115kV GOAB, tap L523 with a 115kV GOAB and build a new 115kV transmission line from Jayess GOAB to Little Creek GOAB. Build a new 115kV breaker switching station at Jayess and build a new 115kV breaker switching station at Norfield. | MS | MS | Current radial transmission service violates MW-Mile planning criteria. |  |  |  | 2024-04-01 | 2024-04-01 | 115 | 0 | Y | 11360000 | Bottom-Up
B in MTEP19 | B | South | Entergy-MS | 15850 | Olive Oil Loop Project | Rebuild L546 (Pisgah GOAB to Magee Road SS) with sufficient ACSR conductor. Rebuild L547 (Arlington GOAB to Arlington) with sufficient ACSR conductor. Tap L547 with a 115kV GOAB, tap L576 (Magee Road SS to Olive Oil) with a 115kV GOAB and build a new 115kV transmission line from Arlington GOAB to Olive Oil GOAB. Build a new 115kV breaker switching station at Arlington. | MS | MS | Current radial transmission service violates MW-Mile planning criteria. |  |  |  | 2024-10-01 | 2024-10-01 | 115 | 0 | Y | 10406000 | Bottom-Up
A in MTEP19 | B>A | West | MDU | 14684 | Miles City | A new 115 kV transmission line from WAPA's Miles City 115 kV Substation to a new Miles City SW 115/60 kV Substation. The new Miles City SW substation will connect to the existing Miles City-Rosebud 60 kV line. | MT | MT | Add a second/redundant source for the Miles City 60 kV system. | Other |  | Other Local Needs | 2020-12-31 | 2020-12-31 | 115 | 60 | Y | 6600000 | Bottom-Up
A in MTEP19 | B>A | West | MDU | 15748 | Baker-Glendive 60 kV | Rebuild Baker-Glendive 60 kV line | MT | MT | Line needs to be rebuild due to age & condition | Other |  | Age and Condition | 2021-12-31 | 2021-12-31 | 60 | 0 | Y | 16900000 | Bottom-Up
A in MTEP19 | B>A | West | MDU | 15771 | Plentywood Loop | Build a 60 kV loop line around Plentywood, MT | MT | MT | Low voltages for loss of Plentywood Substation to Plentywood Town | Other |  | Reliability | 2020-12-31 | 2020-12-31 | 60 | 0 | Y | 2000000 | Bottom-Up
A in MTEP19 | B>A | West | MDU | 15772 | Cabin Creek Breaker | Add 60 kV breaker and bay to split the Cabin Creek-Plevna and the Cabin Creek-North Baker 60 kV line onto separate breakers | MT | MT | Reduce system exposure, simplify relaying, allows for parallel 60 kV support between Cabin Creek and Baker | Other |  | Other Local Needs | 2021-03-31 | 2021-03-31 | 60 | 0 | Y | 600000 | Bottom-Up
A in MTEP19 | B>A | West | MDU | 15777 | Rosebud-Forsyth 60 kV | Rebuild Rosebud-Forsyth 60 kV line | MT | MT | Age & Condition | Other |  | Age and Condition | 2020-12-31 | 2020-12-31 | 60 | 0 | Y | 2000000 | Bottom-Up
A in MTEP19 | B>A | West | MDU | 16125 | Keystone XL PS #14 | A new tap on the Baker-Cabin Creek 115 kV line and radial line to distribution substation | MT | MT | New Keystone XL pump station #14 load | Other |  | Load Growth | 2020-06-30 | 2020-06-30 | 115 | 6 | Y | 3015000 | Bottom-Up
A in MTEP20 | B>A | West | MDU | 15784 | Zahl-Corinth 60 kV line | Rebuild Zahl-Corinth 60 kV line | ND | ND | Age and Condition |  |  |  | 2023-09-30 | 2023-09-30 | 60 | 0 | Y | 3500000 | Bottom-Up
A in MTEP20 | B>A | West | MDU | 17304 | G359, Ellendale 345 Network Upgrades | G359 Network Upgrades at Ellendale 345: four 230 kV 50 Mvar fast-switched capacitors and a new switcher for the 345 kV line reactor on the Big Stone South line | ND | ND | Network Upgrades on the MDU Transmission System need for GI G359, Merricourt. |  |  |  | 2020-02-28 | 2020-02-28 | 345 | 0 | Y | 6431000 | Bottom-Up
A in MTEP20 | B>A | West | MDU | 17466 | Heskett Substation Retirement | The Heskett 230/115/69/41.6 kV substation will be retired due to the retirement and decommissioning of Heskett generators #1 & #2 and because of age and condition concerns. The existing Mandan substation will be expanded to accommodate the 230 and 115 kV facilities and a new Mandan 38th St substation will be constructed to accommodate the 69 and 41.6 kV facilities. | ND | ND | The Heskett 230/115/69/41.6 kV substation will be retired due to the retirement and decommissioning of Heskett generators #1 & #2 and because of age and condition concerns. The existing Mandan substation will be expanded to accommodate the 230 and 115 kV facilities and a new Mandan 38th St substation will be constructed to accommodate the 69 and 41.6 kV facilities. |  |  |  | 2020-09-30 | 2023-06-30 | 230 | 41.6 | Y | 24000000 | Bottom-Up
A in MTEP20 | B>A | West | MDU | 18254 | Tioga Substation Rebuild | Rebuild Tioga substation due to age and condition | ND | ND | Rebuild Tioga substation due to age and condition |  |  |  | 2021-12-31 | 2021-12-31 | 115 | 60 | Y | 2600000 | Bottom-Up
A in MTEP20 | B>A | West | MPC | 17305 | Center Plant 230 kV Line Reroute #2 | Reroute Center-Roughrider 230 kV and Center-Square Butte 230 kV around the Milton R. Young Plant (Center, ND) to accommodate new construction. Additional line miles for each line are 0.2 miles. | ND | ND | Reroute to accommodate new construction. | [5 empty] | 230 | 0 | Y |  | Bottom-Up
A in MTEP20 | B>A | West | XEL | 15737 | Sheyenne Cap Bank Retirement | Remove the 5, 40MVAR fast switched cap banks at Sheyenne. | ND | ND | CAPX Fargo project removed the need for these capacitor banks for voltage stability. Removes maintenance and replacement concerns for aging fast-switch cap banks. | Other |  | Other Local Needs | 2020-03-15 | 2020-03-15 | 115 | 0 | Y | 750000 | Bottom-Up
A in MTEP19 | B>A | West | MDU | 15746 | Beulah-Mandan 115 Rebuild | Rebuild Beulah-Mandan 115 kV and build a new 115 segment to terminate at Coyote | ND | ND | Age and condition of existing Beulah-Mandan 115 kV line. Add Coyote terminal to retire 115 kV thermal RAS at Coyote. | Other |  | Age and Condition | 2021-12-31 | 2021-12-31 | 115 | 0 | Y | 26900000 | Bottom-Up
A in MTEP19 | B>A | West | MDU | 15747 | Merricourt 230/41.6 | Add 230/41.6 kV transformer and 41.6 ring bus at Merricourt Substation. Build Merricourt-Ashley 41.6 kV line and Merricourt-Fredonia 41.6 kV line. | ND | ND | Low voltages on 41.6 kV system for various contingencies | Other |  | Reliability | 2022-12-31 | 2022-12-31 | 230 | 41.6 | Y | 12100000 | Bottom-Up
A in MTEP19 | B>A | West | MDU | 15780 | Lignite-Kincaid 60 kV | Build new Lignite-Kincaid 60 kV line | ND | ND | Allows Kincaid 60 kV switching station to be retired | Other |  | Age and Condition | 2021-03-31 | 2021-03-31 | 60 | 0 | Y | 3100000 | Bottom-Up
A in MTEP19 | B>A | West | MDU | 16124 | Dickinson Refinery | New 115 kV substation with distribution transformer on the Dickinson North-Dickinson West 115 kV line | ND | ND | Load growth | Other |  | Load Growth | 2020-03-31 | 2020-03-31 | 115 | 0 | Y | 7000000 | Bottom-Up
A in MTEP19 | B>A | West | MPC | 15666 | Center Plant 230 kV Line Reroute | Reroute Center-Square Butte 230 kV and Center-Roughrider 230 kV around the Young 1/2 (Center) plant, adding 0.4 miles to each line. | ND | ND | Reroute is required to provide access to the coal pile expansion and provide space for Project Tundra (new facilities at the plant). | Other |  | Other Local Needs | 2019-05-01 | 2019-05-01 | 230 | 0 | Y | 2000000 | Bottom-Up
A in MTEP19 | B>A | West | OTP | 16146 | Jamestown NW Substation 115 kV | New Substation delivery to the 41.6 kV on the West side of Jamestown. The project will consist of - One 115kV Circuit Breaker and one 41.6 kV Circuit Breaker and a 25 MVA transformer. | ND | ND | Improves reliability by introducing a new high voltage transmission source from a 115 to a 41.6 kV transmission system. | Other |  | Reliability | 2021-11-30 | 2021-11-30 | 115 | 41.6 | Y | 3000000 | Bottom-Up
A in MTEP19 | B>A | West | OTP | 16485 | OTP Hankinson to Ellendale 230kV Network Upgrades – J436/J437 | This project consists of upgrades to Otter Tail Power Company’s substations and transmission lines to accommodate the interconnection of two wind generators, J436 and J437, to the Big Stone South to Ellendale 345 kV transmission line. Five Facility upgrades are needed: • Forman to Hankinson 230 kV line • Forman substation • Forman to Oakes 230 kV line • Oakes substation • Oakes to Ellendale 230 kV line | ND | ND | Network Upgrades to the Transmission Owner’s substations and transmission lines required for the interconnection of the Interconnection Customers’ Projects J436 and J437. | GIP |  |  | 2019-09-01 | 2019-11-01 | 230 | 0 | Y | 1439902 | Externally Driven
A in MTEP19 | B>A | West | OTP | 16805 | OTP Deuel Switching Station - J526 | Interconnection Customer J526 will be interconnecting a total of 300 MW wind located in Deuel County, SD. The project will install two separate 34.5 kV collector systems with approximately 150 MW on each collector system. There will be two 166 MVA 34.5/13.8/345 grounded/delta/wye transformers for each of the collector systems. The collector substation will be located approximately 0.2 miles from the Deuel Switching Station with a single 345 kV lead line connecting the collector substation and the new Deuel Switching Station. | SD | ND | Deuel Switching Station will tap the Big Stone South to Brooking County 345 kV transmission line, modification will also be made to the BSSB Line. The upgrades addressed in this Facility Study are for MISO Project J526 include: Deuel County Switching Station, Big Stone South Substation Relay Modifications, BSSB Line In and Out 345 kV line modification, Transmission Owner Interconnection Facilities, Wahpeton to Fergus Falls 230 kV Line Upgrade and Wahpeton 230 kV Substation upgrade. | GIP |  |  | 2020-06-29 | 2020-06-29 | 345 | 0 | Y | 11886510 | Externally Driven
A in MTEP19 | B>A | West | OTP | 16924 | OTP Hankinson to Ellendale 230kV Network Upgrades - J488 | This project consists of upgrades to Otter Tail Power Company’s substations and transmission lines to accommodate the interconnection of a wind generator, J488, to the Big Stone South to Ellendale 345 kV transmission line. Four Facility upgrades are needed: • Forman to Hankinson 230 kV line • Forman substation • Forman to Oakes 230 kV line • Oakes to Ellendale 230 kV line | ND | ND | Network Upgrades to the Transmission Owner’s substations and transmission lines required for the interconnection of the Interconnection Customers’ Project J488. | GIP |  |  | 2019-08-23 | 2020-07-23 | 230 | 0 | Y | 2628468 | Externally Driven
A in MTEP19 | B>A | West | OTP | 17005 | OTP Hankinson to Wahpeton 230 kV Network Upgrades - J460/J488/J493/J526 | This project consists of upgrades to Otter Tail Power Company’s Hankinson to Wahpeton 230 kV transmission line to accommodate the interconnection of wind generators, J460/J488/J493/J526. | ND | ND | Network Upgrades to the Transmission Owner’s transmission line required for the interconnection of the Interconnection Customers’ Project J460/J488/J493/J526. | GIP |  |  | 2020-08-13 | 2020-08-13 | 230 | 0 | Y | 1596087 | Externally Driven
A in MTEP19 | B>A | West | OTP | 17007 | OTP Hankinson to Oakes 230 kV & Big Stone to Blair 230 kV Network Upgrades - G359R | This project consists of upgrades to Otter Tail Power Company’s transmission lines to accommodate the interconnection of G359R. Three Facility upgrades are needed: • Forman to Hankinson 230 kV line • Forman to Oakes 230 kV line • Big Stone to Blair 230 kV line | SD | ND | Network Upgrades to the Transmission Owner’s transmission lines required for the interconnection of the Interconnection Customer Project G359R. | GIP |  |  | 2020-08-31 | 2020-08-31 | 230 | 0 | Y | 1364550 | Externally Driven
A in MTEP19 | B>A | West | OTP | 17024 | OTP Blair 230 kV Substation Switches - J488/J493/J526 | This project upgrades two 230 kV breaker disconnect switches in the Blair Substation. | ND | ND | Network Upgrades to the Transmission Owner’s switches required for the MISO Interconnection Projects J488/J493/J526. | GIP |  |  | 2019-07-01 | 2019-07-01 | 230 | 0 | Y | 70000 | Externally Driven
A in MTEP19 | B>A | West | XEL | 15723 | Prairie Cap Bank Removal | Remove 6 of the 12, 40 MVAR fast switched cap banks at Prairie. Remove 5 of 6 fast switch controls from remaining 40 MVAR cap banks | ND | ND | Changing transmission system no longer requires the capacitors for voltage support. High voltage conditions occur with more than 6 cap banks on. CAPX Fargo project added support to remove the need for fast switching on 5 of 6 remaining cap banks. Unnecessary costs incurred by maintaining and replacing aging capacitor banks that are no longer needed. | Other |  | Other Local Needs | 2020-01-15 | 2020-01-15 | 115 | 0 | Y | 725000 | Bottom-Up
B in MTEP20 | B | West | MDU | 18264 | Halliday Sub-Halliday Rebuild | rebuild Halliday sub-Halliday 41.6 kV line | ND | ND | Improve system voltage, age & condition |  |  |  | 2022-12-31 | 2022-12-31 | 41.6 | 0 | Y | 800000 | Bottom-Up
B in MTEP19 | B | West | MDU | 15785 | Kenmare-Mohall 60 kV | Rebuild Kenmare-Mohall 60 kV line | ND | ND | Age & Condition. Low voltage on 60 kV system for loss of Kenmare Substation-Kenmare West 60 kV line. |  |  |  | 2023-12-31 | 2023-12-31 | 60 | 0 | Y | 5300000 | Bottom-Up
B in MTEP19 | B | West | MDU | 15787 | Kenmare 60 kV Substation | Build new Kenmare 60 kV substation | ND | ND | Age & condition of existing Kenmare 60 kV bus and equipment. Improve reliability and operations by replacing old breaker bypass bus with ring bus. |  |  |  | 2022-06-30 | 2022-06-30 | 115 | 60 | Y | 6525000 | Bottom-Up
B in MTEP19 | B | West | MDU | 15788 | Hettinger 115/69 kV Substation | Replace existing 41.6/69 kV transformer with a new 115/69 kV transformer. Build new 115 kV ring bus to replace existing 115 kV main & transfer bus. | ND | ND | New 115/69 transformer is need to support 69 kV system out of Hettinger. The existing transformer is too small, 6 MVA, to provide support to Elgin for loss of any section of the Heskett-Devaul 69 kV line. The short circuit strength on the 69 kV when sourced from Hettinger is weak and makes relay coordination difficult. The new 115/69 transformer will improve short circuit strength and relaying. There are not any 115 bays available for expansion on the main & transfer bus, so new ring bus will be constructed. | Other |  | Reliability | 2021-12-31 | 2021-12-31 | 115 | 69 | Y | 6900000 | Bottom-Up
B in MTEP19 | B | West | MPC | 17424 | Lake Ardoch 230/115 kV | A 230/115 kV tap on the Prairie-Drayton 230 kV line with a 4 mile 115 kV line to the existing Oslo 115 kV substation. Addition of 4 breaker ring at Oslo 115 kV. | ND | ND | Overloads along Winger-TRF 115 kV during Donaldson breaker fail contingencies and low voltages in the out year models for loss of one of the sources into NW MN. |  |  |  | 2023-12-31 | 2023-12-31 | 230 | 0 | Y |  | Bottom-Up
B in MTEP19 | B | West | OTP | 15728 | Abercrombie 41.6 kV Cap Bank | New 41.6 cap bank (1x3 Mvar) will be installed at OTP's Abercrombie 41.6 kV Substation. | ND | ND | Studies have shown due to existing load and load growth this 41.6 kV cap bank are needed for voltage support. | Other |  | Load Growth | 2020-11-30 | 2020-11-30 | 41.6 | 0 | Y | 1000000 | Bottom-Up
B in MTEP19 | B | West | OTP | 16284 | Buffalo to Enderlin 115 kV Line Reconductoring | Reconductor 7 miles with new 1/0RT2 conductor. Rest of the line will stay with 266R conductor. | ND | ND | Age and condition of 7 miles between Buffalo-Enderlin 115 kV transmission line will be reconductored. Multi-year project being done for reliability. | Other |  | Age and Condition | 2020-12-30 | 2020-12-30 | 115 | 0 | Y | 4000000 | Bottom-Up
B in MTEP19 | B | West | OTP | 16285 | Gackle to Streeter 41.6 kV Line Reconductor | Due to reliability OTP will reconductor 2 miles with new 1/0RT2 conductor. | ND | ND | Age and condition of 2 miles between Gackle to Streeter 41.6 kV transmission line will be reconductored. | Other |  | Age and Condition | 2020-12-30 | 2020-12-30 | 41.6 | 0 | Y | 600000 | Bottom-Up
B in MTEP20 | B | West | MDU | 18261 | Wishek-Greenway Rebuild | rebuild Wishek-Greenway Tap 41.6 kV line | ND,SD | ND,SD | Improve system voltage, age & condition |  |  |  | 2023-12-31 | 2023-12-31 | 41.6 | 0 | Y | 6300000 | Bottom-Up
A in MTEP20 | B>A | West | MDU | 18257 | Greenway Substation | Build three breaker 41.6 kV ring bus on at junction of three terminal Wishek-Bowdle-Glenham 41.6 kV line. | SD | SD | Improve relaying, reduce exposure and improve load serving |  |  |  | 2021-12-31 | 2021-12-31 | 41.6 | 0 | Y | 3100000 | Bottom-Up
A in MTEP20 | B>A | West | MDU | 18260 | Greenway Tap-Herried Rebuild | Rebuild Greenway Tap-Herried 41.6 kV line | SD | SD | Improve system voltage, age & condition |  |  |  | 2021-12-31 | 2021-12-31 | 41.6 | 0 | Y | 6600000 | Bottom-Up
A in MTEP19 | B>A | West | MDU, NWEC, OTP | 16965 | OTP Big Stone Plant 230/115 kV Transformer - J488/J493/J526 | MISO Generator Interconnection projects J488, J493 and J526 require an installation of a new 336 MVA 230/115 kV transformer and associated terminal equipment at the Big Stone Plant 230 kV substation. The existing 230/115 kV transformer at the Big Stone Plant 230 kV Substation will remain intact to the 230 kV and 13.8 kV systems to serve the existing load. The 115 kV side of the existing transformer will be disconnected. | SD | SD | Required network upgrades for MISO generator interconnection projects J488, J493 and J526. | GIP |  |  | 2020-09-24 | 2020-10-01 | 230 | 13.8 | Y | 3389282 | Externally Driven
A in MTEP19 | B>A | West | MDU, NWEC, OTP | 16991 | OTP Big Stone to Blair 230 kV - J488/J493/J526 | MISO Generator Interconnection projects J488, J493 and J526 require the installation of a new 230 kV Switch with operating hardware, removal of existing wave trap and new jumpers and CT adjustments. | SD | SD | Required network upgrades for MISO generator interconnection projects J488, J493 and J526. | GIP |  |  | 2020-10-01 | 2020-10-01 | 230 | 0 | Y | 38440 | Externally Driven
A in MTEP19 | B>A | West | MDU, OTP | 15304 | OTP Twin Brooks 345kV Switching Station - J436/J437 | Interconnection Customer J436 and J437 will be interconnecting a total of 300 MW's into the Big Stone South to Ellendale 345 kV line. In order to interconnect projects J436 and J437 a new 345 kV switching station, designated Twin Brooks, will be constructed approximately 30 line miles west of the Big Stone South Substation on the Big Stone South to Ellendale 345 kV line. | SD | SD | Transmission Owner Network Upgrades will consist of the new Twin Brooks 345 kV Switching Station, Big Stone South to Ellendale 345 kV in and out line modifications, and Big Stone South relay modifications. Transmission Owner Interconnection Facilities will consist of necessary equipment to terminate in the Twin Brooks 345 kV Switching Station, and necessary metering, communication and commissioning. | GIP |  |  | 2020-07-06 | 2020-07-06 | 345 | 0 | Y | 11393377 | Externally Driven
A in MTEP19 | B>A | West | MDU, OTP | 16825 | OTP Twin Brooks 345 kV Switching Station Expansion-J488 | Interconnection Customer J488 will be interconnecting a total of 150 MW's into the Twin Brooks 345 kV switching station. In order to interconnect project J488 an expansion to the Twin Brooks 345 kV switching station will be required. | SD | SD | Transmission Owner Network Upgrades will consist of a modification to Twin Brooks 345 kV Switching Station to interconnect project J488. | GIP |  |  | 2020-06-01 | 2020-06-01 | 345 | 0 | Y | 1855260 | Externally Driven
A in MTEP19 | B>A | West | OTP | 15727 | New Effington 230/41.6 kV Substation | New 230/41.6 kV Substation that taps OTP's portion of the Brown's Valley to Hankinson 230 kV line near New Effington, SD. Substation will consist of a three breaker ring bus and a 230/41.6 kV transformer. | SD | SD | Studies have shown due to new loads and load growth has deemed this project necessary for 41.6 kV voltage support. | Other |  | Load Growth | 2020-11-30 | 2020-11-30 | 230 | 41.6 | Y | 5800000 | Bottom-Up
A in MTEP19 | B>A | West | OTP | 16484 | OTP Blair 230kV Substation Upgrade | Due to age and condition it is necessary to replace existing 2 single phase Oil Breakers with 2 new SF6 Breakers, replace the old Westinghouse Relay Panel to a new SEL Relay Panel, replace Digital Relays to new Electromechanical relays, new control house, new relaying and associated equipment (CTs, PTs, etc...), metering and new telecommunications equipment. | SD | SD | Asset Renewal - Breakers, Relays, Metering and Telecommunications | Other |  | Age and Condition | 2019-06-01 | 2019-06-01 | 230 | 0 | Y | 1210000 | Bottom-Up
A in MTEP19 | B>A | West | OTP, XEL | 16964 | OTP Astoria 345kV Switching Station - J493/J510 | Interconnection Customer J493, a 150 MW wind project, and J510, a 284.5 MW gas plant, will be interconnecting into the Big Stone South to Brookings County 345 kV line. In order to interconnect projects J493 and J510 a new switching station, designated Astoria, will be constructed approximately 16 miles North of the Brookings County 345 kV substation on the Big Stone South to Brookings County 345 kV line. | SD | SD | Transmission Owner Network Upgrades will consist of the new Astoria 345 kV Switching Station, Big Stone South to Brookings County 345 kV in and out line modifications, and Big Stone South relay modifications. Transmission Owner Interconnection Facilities will consist of necessary equipment to terminate projects J493 and J510 in to the 345 kV Switching Station, and necessary metering, communication and commissioning. | GIP |  |  | 2020-04-30 | 2020-04-30 | 345 | 0 | Y | 15199506 | Externally Driven
A in MTEP19 | B>A | West | XEL | 16445 | Blazing Star 1 - J460 | Build new 345kV - 34.5kV substation, tapping the 345kV between Brookings County 345kV and Hawks Nest 345kV to support Generator interconnection of 200MW of wind from Blazing Star 1 - J460. | SD | SD | Provide transmission interconnection for 200MW of wind generation. | GIP |  |  | 2019-12-15 | 2019-12-15 | 345 | 0 | Y | 13627000 | Externally Driven
B in MTEP20 | B | West | MDU | 18265 | McIntosh Substation Rebuild | rebuild McIntosh substation | SD | SD | Age & Condition |  |  |  | 2022-12-31 | 2022-12-31 | 115 | 41.6 | Y | 3700000 | Bottom-Up
A in MTEP20 | B>A | South | Entergy-TX | 4799 | Dishman: Construct new substation | Construct new 230kV substation on the Amelia to Helbig 230kV line | TX | TX | New load serving substation | Other |  | Load Growth | 2023-05-01 | 2023-05-01 | 230 | 0 | Y | 17794297 | Bottom-Up
A in MTEP20 | B>A | South | Entergy-TX | 12766 | Junction 138 kV: New Substation | Build new distribution substation. | TX | TX | Distribution System Load Growth. Junction substation will cut in on the Ponderosa to Conroe 138 kV line. | Other |  | Load Growth | 2023-05-01 | 2023-05-01 | 138 | 0 | Y | 24931517 | Bottom-Up
A in MTEP20 | B>A | South | Entergy-TX | 13931 | Bolivar Peninsula T-Line & Substation Phase 1: Siever 138 kV: New Substation | Construct a 138 kV line from Himex to Siever and convert Blue Water to Siever 138 kV substation. | TX | TX | Distribution System Load Growth. | Other |  | Load Growth | 2024-06-01 | 2024-06-01 | 138 | 0 | Y | 79740516 | Bottom-Up
A in MTEP20 | B>A | South | Entergy-TX | 13943 | Southern Point 138 kV: New Substation | Construct a new 138 kV substation that replaces the existing Speedway 138 kV substation. | TX | TX | Distribution System Load Growth. | Other |  | Load Growth | 2023-06-01 | 2023-06-01 | 138 | 0 | Y | 19396596 | Bottom-Up
A in MTEP20 | B>A | South | Entergy-TX | 15648 | Castle 230 kV: New Distribution Station | Cut the Castle 230 kV station in and out on the Ponderosa to Grimes 230 kV line. 230 kV breakers will be installed at Castle. | TX | TX | Distribution load growth. | Other |  | Load Growth | 2024-06-01 | 2024-06-01 | 230 | 0 | Y | 71401618 | Bottom-Up
A in MTEP20 | B>A | South | Entergy-TX | 15649 | Texas 230 kV: New Distribution Station | Cut the Texas substation in and out of the Lewis Creek to Rocky Creek 230 kV line. | TX | TX | Distribution load growth. | Other |  | Load Growth | 2024-06-01 | 2024-06-01 | 230 | 0 | Y | 48519718 | Bottom-Up
A in MTEP20 | B>A | South | Entergy-TX | 18248 | Millbend 138 kV: New Distribution Station | Build ~ 7miles of new transmission line to cut the new Millbend 138 kV station into the existing New Caney to Parkway 138 kV line. | TX | TX | Area load growth. | Other |  | Load Growth | 2024-06-01 | 2024-06-01 | 138 | 0 | Y | 62460356 | Bottom-Up
A in MTEP20 | B>A | South | Entergy-TX | 18251 | Alligator Bayou to Fort Worth 69 kV Rebuild | Rebuild and reconductor the Alligator Bayou to Fort Worth 69 kV line. | TX | TX | Enhanced reliability. Improve the reliability to this area by rebuilding this aging line. | Other |  | Reliability | 2021-06-01 | 2021-06-01 | 69 | 0 | Y | 9790416 | Bottom-Up
A in MTEP20 | B>A | South | Entergy-TX | 18255 | Fort Worth to Kolbs 69 kV Rebuild | Rebuild the 69 kV line between Fort Worth and Kolbs stations. | TX | TX | Enhanced Reliability. Rebuilding this aging line improves the reliability to this area. | Other |  | Reliability | 2022-06-01 | 2022-06-01 | 69 | 0 | Y | 14008330 | Bottom-Up
A in MTEP20 | B>A | South | Entergy-TX | 18259 | Lacon 138 kV: Breaker and feeders | Install a 138 kV breaker at Lacon in the bay looking toward the LNG tap. Also included in this project are distribution feeder additions. | TX | TX | Enhanced Reliability. Adding a breaker reduces the exposure to customers at Lacon to line faults. | Other |  | Reliability | 2022-06-01 | 2022-06-01 | 138 | 0 | Y | 10282558 | Bottom-Up
A in MTEP19 | B>A | South | Entergy-TX | 13941 | Veteran 230 kV: New Substation | Construct a new Veteran 230 kV substation and cut in and out of Lewis Creek - Rocky Creek 230 kV line. | TX | TX | Distribution System Load Growth. | Other |  | Load Growth | 2022-06-01 | 2022-06-01 | 230 | 0 | Y | 34500000 | Bottom-Up
A in MTEP19 | B>A | South | Entergy-TX | 13944 | Colony 230 kV: Construct New Substation | Construct a new 230 kV substation on the Porter to Timberland 230 kV line near Colony Rd. | TX | TX | Distribution System Load Growth | Other |  | Load Growth | 2023-06-30 | 2023-06-30 | 230 | 0 | Y | 36500000 | Bottom-Up
A in MTEP19 | B>A | South | Entergy-TX | 15647 | Dayton Series Capacitor Bank: Operate Normally Open | Operate the Dayton series capacitor bank normally open. Some station and relay work is required to accomplish this. | TX | TX | With future needed substation and transmission additions in the area, there are protection scheme concerns that are alleviated by operating the Dayton series capacitor bank normally open. | Other |  | Reliability | 2021-06-01 | 2021-06-01 | 230 | 0 | Y | 471000 | Bottom-Up
A in MTEP19 | B>A | South | Entergy-TX | 15650 | ONTF 138 kV: New Station | Construct a 138 kV station between the Union and Stonegate 138 kV stations. | TX | TX | Customer driven | Other |  | Reliability | 2020-06-01 | 2020-06-01 | 138 | 0 | Y | 8150000 | Bottom-Up
A in MTEP19 | B>A | South | Entergy-TX | 15734 | Plum Grove substation | Build new distribution substation. Station to be cut into the Entergy's China-Timberland or Porter-Timberland 230 kV line (The exact cut-in to be further determined contingent on the engineering for Entergy Tline and ETEC / Sam Houston substation project). | TX | TX | Distribution System Load Growth | Other |  | Load Growth | 2022-06-01 | 2022-06-01 | 230 | 25 | Y | 8000000 | Bottom-Up
A in MTEP19 | B>A | South | Entergy-TX | 16324 | Foreman 69 kV: New Customer Station | Entergy is proposing to construct a new 69 kV substation (Foreman 69 kV Substation) which will serve an existing industrial customer’s ~22 MW of load in Orange County, TX. The new 69 kV station will be cut in on Line 561 between the existing Gulfrich and Crown Orange 69 kV stations. Approximately .15 miles of looped transmission will be extended to the Foreman station, which will be a 4 breaker ring bus. | TX | TX | This project is driven by a new Industrial Customer Interconnection. | Other |  | Load Growth | 2019-12-31 | 2019-12-31 | 69 | 0 | Y | 12166125 | Bottom-Up
A in MTEP19 | B>A | South | Entergy-TX | 16572 | J483 Interconnection: Construct 138 kV Switching Substation | Construct a 138 kV 3 breaker ring bus cut into the Stilson to Gordon 138 kV line. | TX | TX | The new station is to accommodate the J483 solar facility. | GIP |  |  | 2020-09-01 | 2020-09-01 | 138 | 0 | Y | 9540000 | Externally Driven
A in MTEP19 | B>A | South | Entergy-TX | 17611 | Star Bayou 230 kV: New Customer Substation | Entergy is proposing to construct a new 230 kV substation (Star Bayou 230 kV Substation) which will serve an industrial customer’s 3.8 MW of existing load in addition to 14 MW of new load in Orange County, TX. The new lines into the Star Bayou substation will be cut in and out (~.3 miles one way) of the existing Helbig to Georgetown 230 kV line 421. The Star Bayou 230 kV station will be constructed as a 3 breaker ring bus. | TX | TX | New 230 kV Customer Substation | Other | Not Shared | Load Growth | 2020-06-01 | 2020-06-01 | 230 | 0 | Y | 11927650 | Bottom-Up
B in MTEP20 | B | South | Entergy-TX | 18262 | Tarkington to New Long John 138 kV: Rebuild Line | Rebuild Tarkington to New Long John (L870). | TX | TX | NERC TPL-001-4 Reliability Standards and Entergy's Planning Guidelines. This project replaces the Pony project. Tarkington to New Long John 138 kV line overloads for the loss of Porter to New Caney 138 kV line. |  |  |  | 2026-06-01 | 2026-06-01 | 138 | 0 | Y | 15523373 | Bottom-Up
B in MTEP20 | B | South | Entergy-TX | 18266 | New Long John to Dayton 138 kV: Rebuild line | Rebuild New Long John to Dayton Bulk 138 kV line. | TX | TX | Enhanced Reliability. The N-1-1 contingency involving the loss of the Lewis Creek to Commerce and Cleveland to Jacinto 138 kV lines results in up to 200 MW of non-consequential load loss. |  |  |  | 2027-06-01 | 2027-06-01 | 138 | 0 | Y | 13949356 | Bottom-Up
A in MTEP20 | B>A | West | ATC | 10590 | Academy – Columbus, 69kV (Y-21), rebuild & OPGW | Rebuild Academy - Columbus (Y-21) 69kV | WI | WI | Asset Renewal - Line Rebuild |  |  |  | 2023-12-31 | 2023-12-31 | 69 | 0 | Y | 3500000 | Bottom-Up
A in MTEP20 | B>A | West | ATC | 12175 | West Middleton – Stage Coach 69 kV (6927), partial rebuild | *Replace the underground cable at West Middleton with a overhead line *Replacement of jumpers, switches and other terminal equipment | WI | WI | Reliability |  |  |  | 2023-12-31 | 2023-12-31 | 69 | 0 | Y | 2735023 | Bottom-Up
A in MTEP20 | B>A | West | ATC | 15930 | Pulliam SS, Transformer Retirement and Bus Reconfiguration | -Removal of Transformer T16 coordinated with retirement of Pulliam Generation Station -Bus Reconfiguration, straight bus to ring bus -Additional asset renewal of relays and removal of unnecessary circuit breakers | WI | WI | Asset Renewal - Substation | Other |  | Age and Condition | 2022-12-31 | 2022-12-31 | 138 | 69 | Y | 4000000 | Bottom-Up
A in MTEP20 | B>A | West | ATC | 16486 | Arcadian SS - Power Transformer and Control House Replacement and Asset Renewal | Renew power transformers, control house, relays, breakers, switches | WI | WI | Asset Renewal - Substation | Other |  | Age and Condition | 2023-12-31 | 2023-12-31 | 345 | 138 | Y | 40000000 | Bottom-Up
A in MTEP20 | B>A | West | ATC | 16606 | Morgan Substation - Breaker Renewal and Facility Upgrades | Morgan Substation - Breaker Renewal and Facility Upgrades | WI | WI | Age and Condition - Substation |  |  |  | 2023-12-01 | 2023-12-01 | 345 | 138 | Y | 5399000 | Bottom-Up
A in MTEP20 | B>A | West | ATC | 17585 | Colley Road SS, Transformer Replacement and Breaker & Relay Asset Renewal | • Replace 1975 vintage 93 MVA 138/69/12.47 kV power transformer with a 100 MVA new purchase • Replace four sets of three-phase 1960’s vintage hook-stick disconnect switches | WI | WI | Age & Condition - Substation |  |  |  | 2023-12-31 | 2023-12-31 | 138 | 69 | Y | 3150000 | Bottom-Up
A in MTEP20 | B>A | West | ATC | 17628 | Preble SS, DIC, add 4th transformer and substation rebuild | WPS will: • expand Preble Substation and install a new control house • add the 4th 138/24.9 kV, 22 MVA xfmr with a circuit breaker on the high-side • rebuild and relocate Bank 2 xfmr and upgrade the high-side to a circuit breaker • retire and remove Henry St Substation ATC will: • extend 138 kV bus to the north and the south • relocate both 138 kV line terminals for line X-154 (Highway V – Tower Dr) • replace existing 77/88 MODs with 138 kV line breakers • install a 138 KV bus-tie breaker • retire the 69 kV Henry St Tap on line L-64 (Danz Ave – Finger Road) | WI | WI | Load Interconnection |  |  |  | 2022-06-01 | 2022-06-01 | 138 | 0 | Y | 3498694 | Bottom-Up
A in MTEP20 | B>A | West | ATC | 18017 | Petenwell-Badger West-Saratoga, (X-43) 138kV Line Rebuild | 138 kV Line X-43 is 22.7 miles long with pole vintages from the 1940s, 1950s and 1960s The limitations of the system result in voltage collapse for forced outages during planned maintenance The Council Creek SPS no longer fully mitigates market congestion issues due to increased system flows X-43 will be rebuilt with an a maximum rating of 1030 Amps for all seasons. This will resolve system reliability, market congestion and pending asset renewal issues | WI | WI | System voltage collapse for Planned or Forced outage P6 scenarios Market congestion even with deployment of the Council Creek SPS Asset Renewal needs for select wood poles on this line |  |  |  | 2022-12-31 | 2022-12-31 | 138 | 0 | Y | 20026000 | Bottom-Up
A in MTEP20 | B>A | West | ATC | 18019 | Glenview SS, Transformer Retirement and Breaker & Relay Asset Renewal | Transformer Retirement Breaker and Relay Asset Renewal | WI | WI | Asset Renewal - Substation |  |  |  | 2023-12-31 | 2023-12-31 | 138 | 69 | Y | 4799000 | Bottom-Up
A in MTEP20 | B>A | West | XEL | 17984 | New Turtle Lake Sub | A new substation will be built to replace existing distribution Turtle Lake sub allow future load. Existing Turtle Lake sub will be retired once distribution conversion is complete. | WI | WI | A new substation will be built to replace existing distribution Turtle Lake sub allow future load. Existing substation wood structure condition is suspect and has inadequate clearances. |  |  |  | 2021-06-15 | 2021-06-15 | 69 | 23.9 | Y | 700000 | Bottom-Up
A in MTEP20 | B>A | West | XEL | 18006 | Osprey - Hawkins 115kV Rebuild | Wreck out and rebuild of approximately 11.36 miles of 115kV line between Osprey and Hawkins substations for aging conditions | WI | WI | Rebuilld 11.36 miles of 115kV line between Osprey to Hawkins to remediate aging conditions on line that have resulted in reliability issues. |  |  |  | 2022-06-15 | 2022-06-15 | 115 | 0 | Y | 8500000 | Bottom-Up
A in MTEP20 | B>A | West | XEL | 18007 | Prentice - Phillips 115kV Rebuild | Complete wreck out and rebuild of 14.8 miles of 115kV line from Prentice to Phillips Tap to remediate aging condition issues. | WI | WI | Rebuild of 14.8 miles of 115kV line from Prentice - Phillips Tap needed to remediate reliability issues caused by aging condition of the line. |  |  |  | 2023-01-31 | 2023-01-31 | 115 | 0 | Y | 10000000 | Bottom-Up
A in MTEP20 | B>A | West | XEL | 18130 | Port Wing - Cornucopia 34.5kV Rebuild | Rebuild 9.6 miles of 34.5kV line from Port Wing to Cornucopia to remediate aging condition issues. | WI | WI | 34.5kV line from Port Wing to Cornucopia is at end of useful life, rebuild needed to remediate reliability concerns due to aging condition of line. |  |  |  | 2023-06-15 | 2023-06-15 | 34.5 | 0 | Y | 5000000 | Bottom-Up
A in MTEP20 | B>A | West | XEL | 18131 | Orienta Tap - Iron River 34.5kV Rebuild | Rebuild 9 miles of 34.5kV line from former Orienta tap switch to Iron River to remediate aging condition issues | WI | WI | 34.5kV line from former Orienta tap switch to Iron River is at end of useful life. Rebuild needed to remediate reliability concerns due to aging condition. |  |  |  | 2023-06-15 | 2023-06-15 | 34.5 | 0 | Y | 5000000 | Bottom-Up
A in MTEP19 | B>A | West | ATC | 4730 | Portage – Columbia 138 kV (X-13/X-20), rebuild existing double circuit | This project is to resolve thermal overloads under single contingency conditions on either the X-13 or X-20 lines between Portage and Columbia. | WI | WI | Reliability | BRP | Not Shared |  | 2024-06-01 | 2024-06-01 | 138 | 0 | Y | 11500000 | Bottom-Up
A in MTEP19 | B>A | West | ATC | 15457 | Summit - Cooney 138kV (6431), rebuild | Rebuild Summit Cooney 138kV (6431) -Line inspection reports indicate line requires rebuild to continue reliable operation -Wood poles show decay, deterioration and woodpecker activity -Rebuild of line consists of 22 H-Frame replacements and 23 single pole structure replacements -Proposed structures shall be designed and sized for T2 477 kcmil ACSR “Hawk” conductors -1950's vintage original construction | WI | WI | Asset Renewal - Line Rebuild | Other |  | Age and Condition | 2023-12-31 | 2023-12-31 | 138 | 138 | Y | 4100000 | Bottom-Up
A in MTEP19 | B>A | West | ATC | 15924 | Danz Ave - University (WPS), 69kV (O-15), underground rebuild & OPGW | *Replace the existing O-15 underground cable sections with XLPE cable installed in existing duct banks and new duct bank roughly adjacent to the existing route of the existing direct buried cables, including new riser structure to the overhead sections of O-16. *Creation of a key fiber loop path will provide: -protection communication -redundant SCADA services to an area with limited access to reliable leased services | WI | WI | Line Rebuild | Other |  | Age and Condition | 2023-12-31 | 2023-12-31 | 69 | 69 | Y | 15850000 | Bottom-Up
A in MTEP19 | B>A | West | ATC | 15925 | Edgewater - Lodestar, 138/69kV, (X-48/Y-31), underground rebuild | Replace the existing X-48/Y-31 underground cable section with XLPE cable installed in a new duct bank and riser structures roughly adjacent to the existing route of the direct buried cables. | WI | WI | Line Rebuild | Other |  | Age and Condition | 2022-12-31 | 2022-12-31 | 138 | 69 | Y | 11400000 | Bottom-Up
A in MTEP19 | B>A | West | ATC | 15928 | Range Line Switchyard, Control House Replacement and Asset Renewal | -Replacement of the inadequate 1970's vintage control house -Replacement of the obsolete solid-state and electromechanical relays with microprocessor relays in the new control house -Replace nine mid-seventies vintage 138 kV oil breakers that are approaching obsolescence and unavailability of replacement parts | WI | WI | Asset Renewal - Substation | Other |  | Age and Condition | 2022-10-31 | 2022-10-31 | 138 | 0 | Y | 7100000 | Bottom-Up
A in MTEP19 | B>A | West | ATC | 15931 | Erdman SS, Transformer and Circuit Breaker Replacements | -Replacement of 138/69kV transformer with 100 MVA on-site spare -Replacement of high-side circuit switcher with a new circuit breaker -Replacement of bus position 138kV oil circuit breaker with new circuit breaker -Additional small asset renewal scope included for efficiency | WI | WI | Asset Renewal - Transformer | Other |  | Age and Condition | 2021-12-01 | 2021-12-01 | 138 | 69 | Y | 7000000 | Bottom-Up
A in MTEP19 | B>A | West | ATC | 15932 | Bain SS, Control House and Relay Replacement | -Construct a new control house including new relays panels and relays -Replacement of 138kV first generation SF6 ABB circuit breaker for asset renewal -Additional asset renewal of arresters and instrument transformers | WI | WI | Asset Renewal - Substation | Other |  | Age and Condition | 2021-12-01 | 2021-12-01 | 138 | 138 | Y | 8500000 | Bottom-Up
A in MTEP19 | B>A | West | ATC | 15935 | Wautoma to Port Edwards, OPGW Installation | Creation of this fiber path will: -improve SCADA reliability and provide protection communications -include a key piece of the chain to tie the Madison area direct-scan fiber cluster to the Appleton-Wausau direct-scan fiber cluster | WI | WI | Communication | Other |  | Other Local Needs | 2021-12-31 | 2021-12-31 | 0 | 0 | Y | 7300000 | Bottom-Up
A in MTEP19 | B>A | West | ATC | 15936 | Stiles - West Marinette, OPGW Installation | Creation of this fiber path will: -Create robust communications infrastructure serving the Marinette - Menominee area -provide a second ATC owned fiber path to Michigan's U.P. -Significantly improves ATC's SCADA reliability in Michigan | WI | WI | Communication | Other |  | Other Local Needs | 2023-12-31 | 2023-12-31 | 0 | 0 | Y | 5600000 | Bottom-Up
A in MTEP19 | B>A | West | ATC | 15947 | Waupaca Area Energy Storage Project | ATC to install a total of 5 MWh of energy storage batteries in the Waupaca area. The battery will be installed on the transmission system to help address maintenance + P1 and P6 issues and will provide operational flexibility. The proposed battery location will be at Harrison North substation, which will consist of 2.5 MW of batteries with 5 MWh of energy. Additionally, an 8 MVAR 138 kV capacitor bank will be installed at the Arnott substation and a 6 MVAR 138 kV capacitor bank will be installed at the Harrison North substation. A bus upgrade will also be completed on the 69 kV Wautoma substation. Communication equipment will be installed for control. ATC is working with a market agent to explore using the battery to provide market services, with the intention of using market revenues to offset the transmission costs to transmission customers associated with this project. | WI | WI | Reliability - Operational Flexibility | Other |  | Reliability | 2021-12-31 | 2021-12-31 | 138 | 13.8 | Y | 8071000 | Bottom-Up
A in MTEP19 | B>A | West | ATC | 16493 | J584 GIC Jordan SS, Generator Interconnection Facilities and Network Upgrades Information | - Construct a new 69-kV substation to interconnect the J584 generation interconnection request. The new substation will be built as a three position ring bus expandable to six positions. The new station will be named "Jordan". - Loop in the existing Blacksmith Tap - Spring Grove Tap 69-kV line (Y-33) to the new station. - Perform required remote end work at Brodhead and South Monroe substations. - Existing redundant fiber (high-speed) communication channels between Brodhead Switching Station and South Monroe will need to be spliced to insert the new J584 Jordan Substation. | WI | WI | GIP | GIP | Not Shared |  | 2021-05-15 | 2021-05-15 | 69 | 0 | Y | 6200000 | Externally Driven
A in MTEP19 | B>A | West | ATC | 16494 | J928 - Garden Corner SS GIC Network Upgrades | J928 Interconnection request is for a new 80 MW wind farm. This will be an expansion of the wind farm that is already at Garden Corners. | WI | WI | GIP | GIP | Shared |  | 2020-06-28 | 2020-06-28 | 138 | 0 | Y | 304855 | Externally Driven
A in MTEP19 | B>A | West | NWEC | 15915 | Frederic-Falun 69KV Old 35 from 350th to 330th | Rebuild the 69KV line with 477 ASCR and horizontal post construction. | WI | WI | To serve load in the area and because of aging pole line. Conductor is presently #4/0 ACSR. | Other |  | Age and Condition | 2020-12-01 | 2020-12-01 | 69 | 0 | Y | 350000 | Bottom-Up
A in MTEP19 | B>A | West | NWEC | 15916 | Frederic-Falun 69KV Old 35 from Elbow Lake Road to 350th | Rebuild the 69KV line with 477 ASCR and horizontal post construction. | WI | WI | To serve load in the area and because of aging pole line. Conductor is presently #4/0 ACSR. | Other |  | Age and Condition | 2021-06-01 | 2021-06-01 | 69 | 0 | Y | 350000 | Bottom-Up
A in MTEP19 | B>A | West | NWEC | 15919 | Frederic-Falun 69KV Elbow Lake Road from County W to Old 35 | Rebuild the 69KV line with 477 ASCR and horizontal post construction. | WI | WI | To serve load in the area and because of aging pole line. Conductor is presently #4/0 ACSR. | Other | Not Shared | Age and Condition | 2021-12-01 | 2021-12-01 | 69 | 0 | Y | 525000 | Bottom-Up
A in MTEP19 | B>A | West | NWEC | 15920 | Lake 26-Tower Road 69KV CCC Road | Rebuild the 69KV line with 477 ASCR and horizontal post construction. | WI | WI | To serve load in the area. Conductor is presently #4/0 ACSR. | Other |  | Reliability | 2022-12-01 | 2022-12-01 | 69 | 0 | Y | 437500 | Bottom-Up
A in MTEP19 | B>A | West | NWEC | 15921 | Lake 26-Tower Road 69KV Lake 26 Road | Rebuild the 69KV line with 477 ASCR and horizontal post construction. | WI | WI | To serve load in the area. Conductor is presently #4/0 ACSR. | Other | Not Shared | Reliability | 2023-12-01 | 2023-12-01 | 69 | 0 | Y | 262500 | Bottom-Up
A in MTEP19 | B>A | West | NWEC | 15922 | Frederic-Coffee Cup 69KV Hwy 35 to Frederic | Rebuild the Dbl Ckt 69KV line with 477ACSR | WI | WI | To serve load in the area. Conductor is presently #1/0 ACSR. | Other | Not Shared | Reliability | 2020-06-01 | 2020-06-01 | 69 | 0 | Y | 450000 | Bottom-Up
A in MTEP19 | B>A | West | XEL | 15724 | Twin Town Substation | Joint Project with DPC to construct a new 69kV line from around structure 240 on line W3429 to the new Twin Town substation, retiring the section north from structure 240 to the DPC Barron to Apple River line and installing a 10 MVAR capacitor bank at Turtle Lake substation. A double circuit line will be built going north from Twin Town to the new Almena DPC substation. One line will connect to the NSP substation Twin Town. The second line will be owned by DPC and connected to the circuit going south to the DPC Clayton substation. | WI | WI | Eliminates a potential three terminal after DPC reconfigures line W3429. Installs a 10MVAR cap bank at Turtle Lake to provide voltage support in the area. | Other |  | Reliability | 2021-01-31 | 2021-01-31 | 69 | 0 | Y | 6400000 | Bottom-Up
A in MTEP19 | B>A | West | XEL | 15726 | Rebuild Clear Lake Sub | Install 2 69kv feeders to new Clear Lake Substation across the street from existing Clear Lake Substation. | WI | WI | Expected load growth makes the existing substation, which is at end of life and has utilized the complete site footprint, inadequate to serve the load. Xcel owns the site across the road from the existing sub, which is large enough to accommodate a second transformer for load growth. | Other |  | Load Growth | 2020-09-15 | 2020-09-15 | 69 | 0 | Y | 4000000 | Bottom-Up
A in MTEP19 | B>A | West | XEL | 15731 | Rebuild Wissota Beach Sub | Install one 69kV feeder and breaker into new Bateman substation on existing site as existing Wissota Beach Substation.. | WI | WI | Substation equipment is at end of life and existing transformer is overloading. | Other |  | Age and Condition | 2020-05-15 | 2020-05-15 | 69 | 0 | Y | 354000 | Bottom-Up
A in MTEP19 | B>A | West | XEL | 15732 | North Menomonie Substation | Install one 69kV feeder and breaker in new Wakanda substation on the north side of Menomonie. | WI | WI | Relieves N-1 risk for 10.8MVA load in Menomonie | Other |  | Reliability | 2020-06-01 | 2020-06-01 | 69 | 12.5 | Y | 345000 | Bottom-Up
A in MTEP19 | B>A | West | XEL | 15733 | Rebuild Elmwood Sub | Expand and rebuild existing Elmwood breaker station including three 69kV breakers and 69kV feeders. | WI | WI | Replaces aging 69-4kV aging substation in poor condition and eliminates reliability and maintenance issues associated with existing 3 way switch. | Other |  | Reliability | 2020-12-15 | 2020-12-15 | 69 | 23.9 | Y | 3180000 | Bottom-Up
A in MTEP19 | B>A | West | XEL | 17125 | Eau Claire Breaker Addition | Adds a new breaker at Eau Claire in place of switch 8E2. This removes a common position between King - Eau Claire 345kV line and TR 9. | WI | WI | This breaker removes a common position between the King - Eau Claire 345kV line and Eau Claire 345-161kV TR 9. The current King - Eau Claire Remedial Action Scheme has been approved to retire and needs this breaker in place before it can be retired. | Other |  | Other Local Needs | 2020-03-15 | 2020-03-15 | 345 | 161 | Y | 900000 | Bottom-Up
B in MTEP20 | B | West | ATC | 17525 | J870/J871 GIC Highland Generator Interconnection Facilities and Network Upgrades | A 300 MW solar farm in Grant and Iowa County, Wisconsin. Customer has requested a Point of Interconnection (POI) at Highland Substation that taps the existing X-17 line between Eden and Wyoming Valley Substations. | WI | WI | Interconnection | GIP |  |  | 2020-08-01 | 2020-08-01 | 138 | 0 | Y | 5754872 | Externally Driven
B in MTEP20 | B | West | ATC | 17526 | J886 GIC Kewaunee SS Interconnection Facilities and Network Upgrades | To modify the existing 138kV Kewaunee Substation to provide transmission interconnection of the J866 with a total summer capacity of 150MW. | WI | WI | Interconnection | GIP |  |  | 2021-05-31 | 2021-05-31 | 138 | 0 | Y | 2293039 | Externally Driven
B in MTEP20 | B | West | ATC | 18046 | Darlington – Rock Branch, (Y-109), 69kV, Rebuild & OPGW | Darlington – Rock Branch, (Y-109), 69kV, Rebuild & OPGW | WI | WI | Asset Renewal - Line Rebuild |  |  |  | 2025-12-31 | 2025-12-31 | 69 | 0 | Y | 1800000 | Bottom-Up
B in MTEP20 | B | West | ATC | 18047 | South Beaver Dam – Horicon, (Y-134), 69kV Rebuild & OPGW | South Beaver Dam – Horicon, (Y-134), 69kV Rebuild & OPGW | WI | WI | Asset Renewal - Line Rebuild |  |  |  | 2025-12-31 | 2025-12-31 | 69 | 0 | Y | 14000000 | Bottom-Up
B in MTEP20 | B | West | ATC | 18048 | Lincoln – Bluemound, (5053), 138kV, Replace with new duct bank and XLPE cable | Lincoln – Bluemound, (5053), 138kV, Replace with new duct bank and XLPE cable | WI | WI | Asset Renewal - Line Rebuild |  |  |  | 2024-12-31 | 2024-12-31 | 138 | 0 | Y | 30000000 | Bottom-Up
B in MTEP20 | B | West | ATC | 18052 | Barneveld SS, DIC, new substation | Barneveld SS, DIC, new substation | WI | WI | Load Interconnection - Coordination with LDC |  |  |  | 2023-12-31 | 2023-12-31 | 69 | 0 | Y | 6000000 | Bottom-Up
B in MTEP20 | B | West | ATC | 18053 | Waupaca SS, DIC, transformer addition | Waupaca SS, DIC, transformer addition | WI | WI | Load Interconnection - Coordination with LDC |  |  |  | 2021-12-31 | 2021-12-31 | 138 | 0 | Y | 6000000 | Bottom-Up
B in MTEP20 | B | West | MP | 17184 | Nemadji Transformer Addition | Expand 115 kV ring bus and add new 115/13.8 kV transformer at Nemadji Switching Station for customer | WI | WI | Customer-requested dedicated source | [5 empty] | 115 | 13.8 | Y | 2500000 | Bottom-Up
B in MTEP20 | B | West | MP | 18062 | Stinson Transmission Line Exits | Reconfigure transmission lines to eliminate line crossing outside of Stinson Substation. Requires a short segment of existing 115 kV line to be rebuilt for 161 kV operation. | WI | WI | Improve safety, access, operations and maintainability |  |  |  | 2022-12-31 | 2022-12-31 | 161 | 0 | Y | 500000 | Bottom-Up
B in MTEP20 | B | West | XEL | 18008 | Ashland to Ironwood 88kV | Rebuild and relocate Bayfront to Norrie 88kV Rebuild and relocate Gingles to Hurley 115kV | WI | WI | Rebuild of existing lines needed to remediate reliability concerns due to aging condition of lines. New right of way needed due to severe environmental and access issues |  |  |  | 2025-12-01 | 2025-12-01 | 115 | 0 | Y | 80000000 | Bottom-Up
B in MTEP19 | B | West | ATC | 15945 | Venus SS, new inductor bank | This project consists of installing a new 115 kV, 10.4 MVAR inductor bank at the Venus substation. | WI | WI | Reliability - Voltage Control | Other |  | Reliability | 2023-12-31 | 2023-12-31 | 115 | 115 | Y | 2500000 | Bottom-Up
B in MTEP19 | B | West | ATC | 16490 | Granville SS, Transformer, Control House and Relay Replacement and Asset Renewal | Renew end-of-life assets including power transformer, control building, breakers, relays, switch | WI | WI | Asset Renewal - Substation | Other |  | Age and Condition | 2024-12-01 | 2024-12-01 | 345 | 138 | Y | 24000000 | Bottom-Up
B in MTEP19 | B | West | ATC | 16495 | Conover – Mass 69kV (6530) Partial rebuild | Re-insulation of approximately 58.0 miles long line and replacement of select pole replacement. | WI | WI | Asset Renewal - Line Rebuild | Other |  | Age and Condition | 2025-12-31 | 2025-12-31 | 69 | 0 | Y | 8600000 | Bottom-Up
B in MTEP19 | B | West | ATC | 16496 | 9 Mile SW STA – Pine River 69kV (6921/23) Partial Rebuild | Re-insulation of approximately 17.0 miles long line and replacement of select cross-arms and select poles. | WI | WI | Asset Renewal - Line Rebuild | Other |  | Age and Condition | 2025-12-31 | 2025-12-31 | 69 | 0 | Y | 5900000 | Bottom-Up
A in MTEP20 | B>A | West | ATC | 14907 | Load Interconnection 2021 | Load Interconnection Project life cycles are customer need driven and typically have shorter project life cycles. These Load Interconnections typically require limited infrastructure modifications and additions. These projects have limited scope and cost. Initial capital spend for this program expected in 2021. | WI,MI | WI,MI | Interconnection |  |  |  | 2024-06-30 | 2024-06-30 | 138 | 69 | Y | 20934210 | Bottom-Up
A in MTEP20 | B>A | West | ATC | 14909 | Small Capital Project and Asset Renewal 2021 | Asset replacements and upgrades typically require limited infrastructure modifications and additions with shorter project life cycles. Transmission Line Projects typically (but not limited to): - Structure, Cross-arm, Insulator, Surge-arrester, and Pole hardware replacements. Substation Projects typically (but not limited to): - Relays, Circuit breakers, Switches, Instrument Transformers (CTs & PTs etc.), Batteries, RTUs, and IT/OT/Communications hardware replacements. Project drivers may be Asset Renewal or small system limit upgrades. These projects have limited scope and cost. Initial capital spend for this program expected in 2021. | WI,MI | WI,MI | Asset Renewal or Reliability |  |  |  | 2024-06-30 | 2024-06-30 | 345 | 69 | Y | 31828256 | Bottom-Up
A in MTEP20 | B>A | West | ATC | 14911 | Communication Reliability Upgrades 2021 | Communications network system upgrades typically require limited infrastructure modifications and additions with shorter project life cycles. Substation Communications Reliability Upgrade projects are typically (but not limited to): - OPGW additions, replacements, relocations, or removals. - Project drivers typically are communications support for SCADA, Relay protection, Security systems, Small communications network upgrades, and Telecom industry market transitions. These projects have limited scope and cost. Initial capital spend for this program expected in 2021. | WI,MI | WI,MI | Communications |  |  |  | 2024-06-30 | 2024-06-30 | 345 | 69 | Y | 15390000 | Bottom-Up
A in MTEP20 | B>A | West | ATC | 14913 | Line Clearance Mitigation Projects 2021 | Line Clearance Mitigation projects have shorter project life cycles. Projects are driven by the ongoing assessment and analysis of field line clearances using Light Detection and Ranging (LiDAR) technology. Clearance mitigation work immediately follows data assessments and issue identification to maintain safety and system reliability. Initial capital spend for this program expected in 2021. | WI,MI | WI,MI | Line Clearance |  |  |  | 2024-06-30 | 2024-06-30 | 345 | 69 | Y | 14800000 | Bottom-Up
A in MTEP20 | B>A | West | ATC | 14915 | Physical Security 2021 | Physical Security projects typically have shorter project life cycles. The Physical Security Program is guided by the NERC Standard CIP-014 and is designed to harden substation infrastructure. Specific project locations and scopes of work are not made public. Initial capital spend for this program expected in 2021. | WI,MI | WI,MI | Physical Security |  |  |  | 2024-06-30 | 2024-06-30 | 345 | 69 | Y | 14299341 | Bottom-Up
A in MTEP19 | B>A | West | ATC | 14906 | Load Interconnection 2020 | Load Interconnection Project life cycles are customer need driven and typically have shorter project life cycles. These Load Interconnections typically require limited infrastructure modifications and additions. These projects have limited scope and cost. Initial capital spend for this program expected in 2020. | WI,MI | WI,MI | Load Interconnection Request | Other |  | Load Growth | 2023-06-30 | 2023-06-30 | 138 | 69 | Y | 26774954 | Bottom-Up
A in MTEP19 | B>A | West | ATC | 14908 | Small Capital Project and Asset Renewal 2020 | Asset replacements and upgrades typically require limited infrastructure modifications and additions with shorter project life cycles. Transmission Line Projects typically (but not limited to): - Structure, Cross-arm, Insulator, Surge-arrester, and Pole hardware replacements. Substation Projects typically (but not limited to): - Relays, Circuit breakers, Switches, Instrument Transformers (CTs & PTs etc.), Batteries, RTUs, and IT/OT/Communications hardware replacements. Project drivers may be Asset Renewal or small system limit upgrades. These projects have limited scope and cost. Initial capital spend for this program expected in 2020. | WI,MI | WI,MI | Asset Renewal or Reliability | Other |  | Age and Condition | 2023-06-30 | 2023-06-30 | 345 | 69 | Y | 35906079 | Bottom-Up
A in MTEP19 | B>A | West | ATC | 14910 | Communication Reliability Upgrades 2020 | Communications network system upgrades typically require limited infrastructure modifications and additions with shorter project life cycles. Substation Communications Reliability Upgrade projects are typically (but not limited to): - OPGW additions, replacements, relocations, or removals. - Project drivers typically are communications support for SCADA, Relay protection, Security systems, Small communications network upgrades, and Telecom industry market transitions. These projects have limited scope and cost. Initial capital spend for this program expected in 2020. | WI,MI | WI,MI | Communications | Other |  | Other Local Needs | 2023-06-30 | 2023-06-30 | 345 | 69 | Y | 11344615 | Bottom-Up
A in MTEP19 | B>A | West | ATC | 14912 | Line Clearance Mitigation Projects 2020 | Line Clearance Mitigation projects have shorter project life cycles. Projects are driven by the ongoing assessment and analysis of field line clearances using Light Detection and Ranging (LiDAR) technology. Clearance mitigation work immediately follows data assessments and issue identification to maintain safety and system reliability. Initial capital spend for this program expected in 2020. | WI,MI | WI,MI | Line Clearance | Other |  | Reliability | 2023-06-30 | 2023-06-30 | 345 | 69 | Y | 12062247 | Bottom-Up
A in MTEP19 | B>A | West | ATC | 14914 | Physical Security 2020 | Physical Security projects typically have shorter project life cycles. The Physical Security Program is guided by the NERC Standard CIP-014 and is designed to harden substation infrastructure. Specific project locations and scopes of work are not made public. Initial capital spend for this program expected in 2020. | WI,MI | WI,MI | Physical Security | Other |  | Other Local Needs | 2023-06-30 | 2023-06-30 | 345 | 69 | Y | 21603965 | Bottom-Up
A in MTEP20 | B>A | South | SMPA | 17004 | Benndale Recip Project | Details to come |  |  | Details to come | [5 empty] | 0 | 0 | Y |  | Bottom-Up
A in MTEP20 | B>A | West | MP | 17869 | Superior Transmission Line Relocations | Relocate transmission lines around industrial site to enable development |  |  | Landowner required relocation | [5 empty] | 0 | 0 | Y |  | Bottom-Up
A in MTEP20 | B>A | West | CMMPA | 18118 | Windom_Transmission_Upgrade | Windom Municipal Utilities (WMU) has two transmission lines that source the Power Plant Substation. The south transmission line is sourced from the ITC substation located south of the city. This line is approximately 1.5 miles. The east transmission line interconnects with an ITC 69 kV transmission line on the east side of the city. This line is approximately 1.36 miles. It appears both transmission lines were constructed circa 1971. WMU has indicated it would like to relocate the south transmission line along the 1st Avenue between the Power Plant substation and 6th Street. This section of line has two overhead distribution circuits under built on the transmission structures. WMU indicated that the distribution lines could be converted to underground. In addition, WMU has requested a cost estimate to construct a new 69 kV transmission to the north of the city for a possible future substation. This new segment would replace the existing east transmission line that interconnects with ITC east of the city. |  |  | The age of the existing transmission lines is nearing 50 years and could be nearing the end of the design life. As inspected by DGR Engineering, some of the structures are starting to show signs of its age. | [5 empty] | 0 | 0 | Y |  | Bottom-Up
A in MTEP20 | B>A | South | SMPA | 18180 | Missionary 230kV Reactor Bank | Add new bay and breaker at Missionary 230 kV substation. Add new Reactor Bank (Single Stage 30 MVAR) at Missionary 230 kV substation. |  |  | During periods of low load and minimal system generation, high voltage is experienced at Cooperative Energy substations. In order to mitigate the high voltage areas, install a reactor at Missionary 230kV substation. | [5 empty] | 0 | 0 | Y |  | Bottom-Up
A in MTEP20 | B>A | South | SMPA | 18182 | Cole Road 69 kV Capacitor Bank | Relocate Paulding 69kV cap bank to Cole Road 69kV substation. |  |  | In order to provide better system voltage support to a heavily loaded area of the system, relocate the Paulding 69kV cap bank to Cole Road 69kV substation. | [5 empty] | 0 | 0 | Y |  | Bottom-Up
A in MTEP20 | B>A | South | SMPA | 18226 | Refuge 115 kV Equipment Upgrade | Cooperative Energy plans to upgrade the 1200 A switch at Refuge Switching Station |  |  | TPL P12 Loss of Andrus to Greenville 115 kV line causes overloads on the Andrus to Refuge 115 kV line. | [5 empty] | 0 | 0 | Y |  | Bottom-Up
B in MTEP20 | B | West | ATC | 16766 | Small Capital Project and Asset Renewal 2023 | sset replacements and upgrades typically require limited infrastructure modifications and additions with shorter project life cycles. Transmission Line Projects typically (but not limited to): - Structure, Cross-arm, Insulator, Surge-arrester, and Pole hardware replacements. Substation Projects typically (but not limited to): - Relays, Circuit breakers, Switches, Instrument Transformers (CTs & PTs etc.), Batteries, RTUs, and IT/OT/Communications hardware replacements. Project drivers may be Asset Renewal or small system limit upgrades. These projects have limited scope and cost. Initial capital spend for this program expected in 2018. |  |  | Other - Age and Condition | [5 empty] | 0 | 0 | Y |  | Bottom-Up
B in MTEP20 | B | West | ATC | 16767 | Communications Reliability Upgrades 2023 | Communications network system upgrades typically require limited infrastructure modifications and additions with shorter project life cycles. Substation Communications Reliability Upgrade projects are typically (but not limited to): - OPGW additions, replacements, relocations, or removals. - Project drivers typically are communications support for SCADA, Relay protection, Security systems, Small communications network upgrades, and Telecom industry market transitions. These projects have limited scope and cost. Initial capital spend for this program expected in 2018. |  |  | Communications | [5 empty] | 0 | 0 | Y |  | Bottom-Up
B in MTEP20 | B | West | ATC | 16768 | Line Clearance Mitigation Projects 2023 | Line Clearance Mitigation projects have shorter project life cycles. Projects are driven by the ongoing assessment and analysis of field line clearances using Light Detection and Ranging (LiDAR) technology. Clearance mitigation work immediately follows data assessments and issue identification to maintain safety and system reliability. Initial capital spend for this program expected in 2023. |  |  | Line Clearance | [5 empty] | 0 | 0 | Y |  | Bottom-Up
B in MTEP20 | B | West | ATC | 16769 | Physical Security 2023 | Physical Security projects typically have shorter project life cycles. The Physical Security Program is guided by the NERC Standard CIP-014 and is designed to harden substation infrastructure. Specific project locations and scopes of work are not made public. Initial capital spend for this program expected in 2023. |  |  | Physical Security | [5 empty] | 0 | 0 | Y |  | Bottom-Up
B in MTEP20 | B | West | ATC | 16770 | Load Interconnection 2023 | Distribution Interconnection Project life cycles are customer need driven and typically have shorter project life cycles. These Distribution Interconnections typically require limited infrastructure modifications and additions. These projects have limited scope and cost. Initial capital spend for this program expected in 2023. |  |  | Interconnection | [5 empty] | 0 | 0 | Y |  | Bottom-Up
B in MTEP20 | B | West | MP | 17868 | Duluth Loop 115 kV Project | Scope TBD |  |  | Voltage collapse for loss of connection to Arrowhead Substation | [5 empty] | 0 | 0 | Y |  | Bottom-Up
B in MTEP20 | B | South | SMPA | 18224 | Batesville 161 kV Bus Reconfigure | Reconfigure the Batesville 161kV substation so that the Batesville - Batesville TVA ties lines do not share a common breaker. |  |  | TPL P23 violations (breaker failures causing the loss of both Batesville - Batesville TVA 161kV tie lines) causes overloads to Entergy Batesville substation. | [5 empty] | 0 | 0 | Y |  | Bottom-Up
B in MTEP19 | B | West | MISO | 17764 | Wilmarth - Faribault - North Rochester 345 kV | Studied during the MN 44 exploratory analysis, this project adds a 345 kV line between Mankato and Rochester. The line will stop at a new 345 kV yard in Faribault to support the local 100 kV system. |  |  | Low voltages exist in the Owatonna and Faribault areas during P2 and P6 events. Load growth has brought the system to capacity. In addition to this, overloads due to future high wind scenarios occur throughout south central MN. | [5 empty] | 0 | 0 | Y |  | Bottom-Up